## Slide 1: Overview of Technical and Policy Challenges in Meeting 2020 Phase Out Targets
on RAC Servicing Sector
- Leakage Control -
The Annual 2017 Network Meetings of the National Ozone Officers of the South Asia Countries
Agra, India, 23-26 May 2017
Niro Tohi
PREC Institute Inc., Japan

## Slide 2: Estimated f-gas emissions in Japan
CFCs/HCFCs have been successfully reduced.
HFCs emissions have been increasing rapidly and are estimated to double in 2020 as compared to emissions in 2011 from RAC (approx. 80% of total).
Estimated f-gas emissions from refrigeration and air-conditioning in 2020

## Slide 3: Estimated f-gas emissions in Japan
It was found out that refrigerant leakage from the equipment in use is going to be much more than expected.
(mil t-CO2)
50
40
30
20
10
Chart: 
| 漏洩量
別置型ショーケース | 9.6
家庭用エアコン | 3.5
その他業務用 | 3.1
ビル用ＰＡＣ | 2.2
その他中型冷凍冷蔵機器 | 1.8
大型冷凍機 | 0.9
小型冷凍冷蔵機器 | 0.1
in use
at disposal
Leakage
2020 BAU
Separated-type Showcases
Room ACs
Commercial ACs
Large refrigerators
Small refrigerators
Packaged ACs for buildings
Middle sized refrigerators
Separated-type Showcase
Outdoor
Indoor
Refrigerator
Showcase
Estimated f-gas emissions and leakages from RAC by type in 2020 (BAU)

## Slide 4: Main causes of refrigerant leakage from RAC equipment in use
Poor maintenance
Aging
Users often do not grasp the situation of leakage and cause(s), and repeat refilling without repairing.

## Slide 5: Responsibilities of Industrial/Commercial RAC Users
Proper management of RAC equipment
Installation at appropriate places/maintaining the appropriate installation environment.
Inspection of equipment

## Slide 6: Inspection frequency required by the law in Japan
Users must carry out simple inspection of all specified products more than once in 3 months.
Temperature inside
Frosts on heat exchanger
Outdoor units
Oil seeping
Corrosion
Damages, abnormal noises & vibrations
Visual inspection and checking for abnormal noises etc.
Inspection items

## Slide 7: Inspection frequency required by the law in Japan
Category | Capacity | Inspection frequency
Refrigerators | 7.5 kW or larger | more than once/year
Air conditioners | 50 kW or larger | more than once/year
 | 7.5 kW or larger (smaller than 50kW) | more than once/3 years
For certain specified products, Periodic Inspection must be carried out by a person with specialized knowledge.

## Slide 8: Example of Periodic Inspection
Direct method
Spray bubbling liquid to detect leakage spots
Electronic leak detectors

## Slide 9: Example of Periodic Inspection
Indirect method
Using a check sheet, check whether the operation values of the running devices are deviated from the daily/normal values and diagnose the possibility of leakage.

## Slide 10: Record-keeping of inspection
Users must keep the record of inspection, the history of repair and filling/recovery of refrigerants.
Related records must be disclosed upon request of a maintenance operators etc. at the time of equipment maintenance.

## Slide 11: Guideline on fluorocarbon leakage inspection and repairing for commercial RAC equipment
The guideline has been developed and published by RAC association (JARAC)
JARAC:
Japan Association of Refrigeration and Air-Conditioning Contractors

## Slide 12: Summary
Responsibilities of industrial/commercial RAC users for refrigerant leakage control
Simple inspection (more frequent)
Periodic inspection (more specialized)
Record-keeping
In order to supervise how equipment are managed, the information of equipment and users/managers is necessary.

## Slide 13
Thank you for your attention