MONTREAL PROTOCOL

ON SUBSTANCES THAT DEPLETE

THE OZONE LAYER

UNEP

Report Of The

Technology and Economic Assessment Panel

June 2016

Decision XXVII/4 Task Force Report

Further Information on Alternatives to

Ozone-Depleting Substances

UNEP

June 2016 Report of the

Technology and Economic

Assessment Panel

Decision XXVII/4 Task Force Report

Further Information on Alternatives

to Ozone-Depleting Substances

Montreal Protocol

On Substances that Deplete the Ozone Layer

Report of the

UNEP Technology and Economic Assessment Panel

June 2016

Decision XXVII/4 Task Force Report:

Further Information on Alternatives to Ozone Depleting Substances

The text of this report is composed in Times New Roman.

Co-ordination:	TEAP and its XXVII/4 Task Force

Composition and layout:	XXVII/4 Task Force co-chairs

Final formatting:	Ozone Secretariat and Lambert Kuijpers

Reproduction:	UNON Nairobi

Date:	June 2016

Under certain conditions, printed copies of this report are available from:

UNITED NATIONS ENVIRONMENT PROGRAMME
Ozone Secretariat, P.O. Box 30552, Nairobi, Kenya

This document is also available in electronic form from http:// ozone.unep.org/en/assessment-panels/technology-and-economic-assessment-panel

No copyright involved. This publication may be freely copied, abstracted and cited, with acknowledgement of the source of the material.

ISBN: 978-9966-076-18-2

UNEP

June 2016 Report of the

Technology and Economic

Assessment Panel

Decision XXVII/4 Task Force Report

Further Information on Alternatives

to Ozone-Depleting Substances

DISCLAIMER

The United Nations Environment Programme (UNEP), the Technology and Economic Assessment Panel (TEAP) co-chairs and members, the Technical Options Committee, chairs, co-chairs and members, the TEAP Task Forces co-chairs and members, and the companies and organisations that employ them do not endorse the performance, worker safety, or environmental acceptability of any of the technical options discussed. Every industrial operation requires consideration of worker safety and proper disposal of contaminants and waste products. Moreover, as work continues - including additional toxicity evaluation - more information on health, environmental and safety effects of alternatives and replacements will become available for use in selecting among the options discussed in this document.

UNEP, the TEAP co-chairs and members, the Technical Options Committee, chairs, co-chairs and members, and the Technology and Economic Assessment Panel Task Forces co-chairs and members, in furnishing or distributing the information that follows, do not make any warranty or representation, either express or implied, with respect to the accuracy, completeness, or utility; nor do they assume any liability of any kind whatsoever resulting from the use or reliance upon any information, material, or procedure contained herein.

Although all statements and information contained in this XXVII/4 report are believed to be accurate and reliable, they are presented without guarantee or warranty of any kind, expressed or implied. Information provided herein does not relieve the reader from the responsibility of carrying out its own tests and experiments, and the reader assumes all responsibility for use of the information and results obtained. Statements or suggestions concerning the use of materials and processes are made without representation or warranty that any such use is free of patent infringement and are not recommendations to infringe on any patents. The user should not assume that all toxicity data and safety measures are indicated herein or that other measures may not be required.

ACKNOWLEDGEMENT

The UNEP Technology and Economic Assessment Panel and the XXVII/4 Task Force co-chairs and members wish to express thanks to all who contributed from governments, both Article 5 and non-Article 5, furthermore in particular to the Ozone Secretariat and the Multilateral Fund Secretariat, as well as to a large number of individuals involved in Protocol issues, without whose involvement this Update Task Force report would not have been possible.

The opinions expressed are those of the Panel and its Task Force and do not necessarily reflect the reviews of any sponsoring or supporting organisation.

# Preface

This report is a follow up to the March 2016 TEAP XXVII/4 Task Force Report, submitted to the OEWG-37 Meeting of the Parties in Geneva, April 2016.

This June 2016 TEAP XXVII/4 Task Force report is being submitted by the TEAP to the 38th Meeting of the Open-ended Working Group of the Parties to the Montreal Protocol, Vienna, July 2016.

The UNEP Technology and Economic Assessment Panel (TEAP):

| Bella Maranion, co-chair | USA | Keiichi Ohnishi | J |
| --- | --- | --- | --- |
| Marta Pizano, co-chair | COL | Fabio Polonara | I |
| Ashley Woodcock, co-chair | UK | Roberto Peixoto | BRA |
| Mohamed Besri | MOR | Ian Porter | AUS |
| Suely Carvalho | BRA | Helen Tope | AUS |
| David Catchpole | UK | Dan Verdonik | USA |
| Marco Gonzalez | CR | Shiqiu Zhang | PRC |
| Sergey Kopylov | RF | Jianjun Zhang | PRC |
| Lambert Kuijpers | NL |  |  |

UNEP

June 2016 Report of the

Technology and Economic Assessment Panel

Decision XXVII/4 Task Force Report

Further Information on Alternatives

to Ozone-Depleting Substances

Table of Contents	Page

Preface	vii

Executive summary	1

ES1.	  Introduction	1

ES2.	  Update on the status of refrigerants	2

ES3.	  Update on R/AC alternative refrigerants and technologies	3

ES4.	 Alternatives to refrigeration systems on fishing vessels	4

ES5.	 Suitability of alternatives under high ambient temperature (HAT) conditions	5

ES6.	  BAU and mitigation demand scenarios for R/AC	5

1	Introduction	9

1.1	Terms of Reference for the XXVII/4 Task Force report	9

1.2	Scope and coverage	9

1.3	Composition of the Task Force and approach	10

2	Update of the status on refrigerants	13

2.1	 Introduction	13

2.2	 Refrigerant data	13

2.3	 Refrigerant classification and standards	20

2.4	 Likelihood of new molecules and new radically different blends	20

2.5	 Road to availability of alternative refrigerants	21

2.6	 Energy efficiency in relation to refrigerants	22

2.7	 Climate impact related to refrigerants	23

2.8	The GWP classification issue	24

2.9	 Environmentally sustainable and environmentally sound	25

2.10	 References	26

3	Update on R/AC alternative refrigerants and technologies	29

3.1	 Domestic Appliances	29

3.2	 Commercial Refrigeration	29

3.3	 Industrial Systems	30

3.4	 Transport refrigeration	31

3.5	 Air-to-air air conditioners and heat pumps	32

3.6	 Water heating heat pumps	32

3.7	 Chillers	33

3.8	 Vehicle air conditioning	35

3.9	 Not-In-Kind technologies	35

3.10	 Developments of CO2 technology	37

3.11 	 Standards in the R/AC industry	38

3.12 	 References	39

4 	Alternatives to refrigeration systems on fishing vessels	41

4.1	Introduction	41

4.2	Considerations and options for replacement and retrofit of refrigeration systems in fishing vessels	41

5	Suitability of alternatives under High Ambient Temperature (HAT) conditions	45

5.1 	 Influence of HAT conditions on R/AC equipment design	45

5.2	 Results from research projects	46

5.2.1	PRAHA project	47

5.2.2	ORNL Project	49

5.2.3	AREP Project	51

5.2.4	General remarks on the three research projects	54

5.3 	Further considerations	55

5.4	References	56

6	BAU and MIT scenarios for Article 5 and non-Article 5 Parties for 1990-2050: Refrigeration and Air Conditioning	59

6.1	 Expansion of scenarios	59

6.2 	 Method used for calculation	60

6.3	 HFC production and demand (consumption) data	62

6.4	 Non-Article 5 scenarios up to 2050	64

6.4.1	BAU scenario	64

6.4.2 	MIT-3 scenario	67

6.4.3 	MIT-5 scenario	69

6.5 	 Article 5 scenarios up to 2050	71

6.5.1	BAU scenario	71

6.5.2	MIT-3 scenario	74

6.5.3 	Impact of manufacturing conversion periods in the MIT-3 scenario	76

6.5.4	MIT-4 scenario	78

6.5.5	Impact of manufacturing conversion periods in the MIT-4 scenario	80

6.5.6	MIT-5 scenario	81

6.5.7	Impact of manufacturing conversion periods in the MIT-5 scenario	82

6.6 	Refrigerant demand and mitigation benefit numbers	83

6.7	 References	91

7	List of acronyms and abbreviations	93

Annex 1 - Summary of Informal Discussion on the TEAP Decision XXVII/4 Task Force Report for OEWG-37	95

Annex 2 - Background information about refrigeration in the fishing industry	97

A2.1	 The fishing industry	97

A2.1.1	Pacific fishing vessels	97

A2.1.2	The EU fishery fleet	100

A2.2	 Refrigeration within the fishing industry	101

A2.2.1	Refrigeration on board	101

A2.2.2	Ice plants and Refrigerated Sea Water (RSW)	102

A2.2.3	Freezer trawlers	102

A2.2.4	Ultra-low temperature freezing	103

A2.3	 Refrigerants currently used	104

A2.3.1	Refrigerants used on board	104

A2.3.2	Refrigerants used on land operations	104

A3.3.3	Refrigerant leakage	104

A2.3.4	High ambient temperatures (HAT)	105

A2.4	 Low-GWP alternatives to ODS refrigerants	105

A2.4.1	Alternatives to HCFC-22	105

A2.4.2	Option 1 – Non-halocarbon refrigerants (R-717 and R-744)	107

A2.4.3	Option 2 – Refrigerant replacement with plant adjustments	109

A2.4.4	Option 3 – Refrigerant drop-in	110

A2.4.5	Option 4 – Maintaining HCFC-22	111

A2.4.6	Ultra-low temperature solutions	111

A2.4.7	Land based equipment	113

A2.4.8	Not-In-Kind technologies	113

A2.5	 References	114

Annex 3 - EU (F-gas, MAC Directive), USA (EPA SNAP Program) and Japan Regulatory Prohibitions (Ch. 6)	116

Annex 4 - Updated Tables for total, new manufacturing, and servicing demand	123

# Executive summary

## ES1.	  Introduction

- Decision XXVII/4 requested TEAP to provide an update of information on alternatives to ozone-depleting substances listed in the September 2015 Update XXVI/9 Task Force report and considering the specific parameters outlined in the current Decision.

- Given that Parties are holding two Open-ended Working Group (OEWG) meetings this year, TEAP has taken the approach to provide two reports responding to Decision XXVII/4. TEAP provided its first March 2016 report to OEWG-37 focused on the refrigeration and air conditioning (R/AC) sector, and included updates on alternatives, results of testing on alternatives under high ambient temperature (HAT) conditions, discussion of other parameters outlined in the decision, and an extension of the mitigation scenarios to 2050.

- After TEAP presented its first report to OEWG-37 and offered clarifications on the information, TEAP received comments from Parties during the plenary discussion of the report as well as during an informal discussion meeting with TEAP, Thursday 7 April. The summary of the informal discussion meeting is provided in Annex 1. The comments have been taken into consideration by the TEAP Decision XXVII/4 Task Force within the timeline remaining to the Task Force to complete its second report for submission to OEWG-38.

- TEAP’s approach with its second report under Decision XXVII/4 is to provide Parties with a single reference document as much as possible for OEWG-38. This second report, therefore, contains much of the same information as in the first report with a focus on the R/AC sector and updates and additions are indicated at the beginning of each chapter or section, as appropriate.

- In particular, TEAP’s second report under Decision XXVII/4 for OEWG-38 provides the following:

  - In Chapter 2, further elaboration is provided on the use of the term “environmentally sound” in response to comments;

  - In response to comments related to further updates and information on refrigerants and not-kind-technologies, this second report includes a new chapter (Chapter 3) providing updates on refrigerant alternatives and technologies;

  - In response to comments related to safety of the new alternatives, this second report elaborates on the technical perspective related to safe use of the refrigerants in the chapter on refrigeration (Chapter 3);

  - A new chapter (Chapter 4) responds to the decision request to provide new and updated information as this is available related to the availability of alternatives for replacement and retrofit of refrigeration systems in fishing vessels, including in small island countries. Related to this chapter, Annex 2 provides additional background information on refrigeration systems in the fishing industry (with particular consideration on the Pacific Islands region);

  - Based on comments related to a more balanced discussion (both positive and negative) of the results of the testing programs for refrigerants under HAT conditions, a revised chapter (Chapter 5) covering these studies is included in this report including summary tables of each of the testing programs;

  - Comments related to scenarios included further information related to HFC production, the magnitude of present banks of HFCs, a business-as-usual (BAU) scenario without and with regulations (see also Annex 3), whether scenarios could be presented on a regional basis, clarification of the estimated growth rates used compared to refrigerant demand growth, consideration of the impacts for a longer manufacturing conversion of 18 years. This issue is addressed in the revised chapter of this second report (Chapter 6) concerning Article 5 mitigation scenarios. Related to this chapter, Annex 4 of this report contains updated tables for total, new manufacturing, and servicing demand.

- Given the short timeline between OEWG-37 and the development of the second Task Force report to OEWG-38, this second report again focused on the R/AC sector. To the extent that updates and new information on alternatives are available to the Task Force, the other sectors (foams, fire suppression, metered dose inhalers (MDIs), other medical and non-medical aerosols, and solvents) will be covered in the Task Force’s update report to MOP-28.The following sections provide the technical summaries of the report’s main chapters. The summaries of the chapters from the first report remain essentially the same as in that report with any update or additional information indicated in bold upfront.

## ES2.	  Update on the status of refrigerants

- Based on comments from Parties on TEAP’s first report to OEWG-37, this chapter includes the following updates and new information:

  - A further elaboration on the use of the term “environmentally sound”.

- Chapter 2 lists 80 fluids which have either been proposed or are being tested in industry programmes, or are pending publication, or have been published in ISO 817 and ASHRAE 34 refrigerant standards since the 2014 RTOC Assessment Report. The majority of these are new mixtures, but traditional fluids and two new molecules are also included. Chapter 2 includes discussions on how refrigerants are classified in refrigerant standards and increased safety risks of some of low-GWP refrigerants that need to be addressed.

- There are alternative refrigerants available today with negligible ODP and lower GWP, however, for some applications it can be challenging to achieve the same lifetime cost level of conventional systems while keeping the same performance and size. The search for new alternative fluids may yield more economical solutions, but the prospects of discovering new, radically different fluids are minimal.

- Market dynamics are critical in the rate of adoption of new refrigerants. There is a limit to the number of different refrigerants that a market (customers, sales channels, service companies) can manage. Hence, companies will be selective about where they launch a product, avoiding areas which are saturated, and promoting sales where they see the greatest market potential.

- It is difficult to assign energy efficiency to a refrigerant, because energy efficiency of refrigeration systems is an additional variable to the refrigerant choice also related to system configuration and component efficiencies. One approach when assessing the energy efficiency related to a refrigerant is to start with a specific refrigerant and use a system architecture suitable for this refrigerant, while comparing to a reference system for the refrigerant to be replaced. Other approaches screen alternative refrigerants suitable for a given system architecture. The common methods can be divided into theoretical and semi-theoretical cycle simulations, detailed equipment simulation models, and laboratory tests of the equipment. In practice, the achievable energy efficiency is limited by the cost of the system, as the success in the market depends on a cost-performance trade-off.

- The difficulties in assessing the total warming impact related to refrigerants is discussed, including the difficulty of defining “low global warming potential”, and assessing the energy efficiency related to the use of a refrigerant.

- Total climate impact related to refrigerants consists of direct and indirect contributions. The direct contribution is a function of a refrigerant’s GWP, charge amount, emissions due to leakage from equipment and those associated with the service and disposal of the equipment. The definition of the qualifiers “high”, “medium” and “low” in relation to GWP is a qualitative, non-technical choice related to what is acceptable in specific applications. The indirect contribution accounts for the CO2-equivalent emissions generated during the production of energy consumed by the refrigeration, air-conditioning, and heat pump equipment. These emissions are affected by equipment's operating characteristics and the emission factor of the local electricity production. Operating characteristics include operating conditions, operating profile, system capacity, system hardware, among others, which makes a comparison difficult in many instances. The indirect contribution is the dominant contributor in very low to no leakage or “tight systems”.

## ES3.	  Update on R/AC alternative refrigerants and technologies

- Based on comments from Parties on TEAP’s first report to OEWG-37, this new chapter provides updates on refrigerant alternatives and technologies, including discussion of Not-In-Kind-technologies and the status of CO2 technologies, and also discusses standards within the R/AC sector; also included is an elaboration on the technical perspective related to safe use of the alternative refrigerants as covered in relevant standards.

- HC-600a and HFC-134a continue to be the primary refrigerant options for production of new domestic refrigeration appliances. It is projected that, by 2020, about 75% of new refrigerator production will use HC-600a, most of the rest will use HFC-134a, and a small share may apply unsaturated HFC refrigerants such as HFO-1234yf.

- In supermarkets, blends such as R-448A, R-449-A, R-449B, R-450A, and R-513A are now beginning to grow in use, starting with Europe and the United States. The same holds true for condensing units and self-contained equipment. In the self-contained equipment category, early trials with HFO-1234yf and HFO-1234ze have started. The use of R-407A and R-407F continues to grow further in many parts of the world.

- Refrigerants such as R-744 are increasingly being used in supermarket systems worldwide – both in cascaded systems (R-744 for low temperature cascaded with a second refrigerant such as HFC-134a or similar and R-717 in limited cases) and in transcritical systems. Transcritical systems are being researched extensively to reduce their energy penalty at high ambient conditions through the use of component and system technologies such as ejector, adiabatic condensing, sub-cooling and parallel compression.

- In industrial refrigeration the major trend, which also is a major challenge, is the focus on refrigerant charge reduction. The market for heat pumps is increasing rapidly. Industrial heat pumps use heat that is considered waste in other parts of production processes.

- In transport refrigeration, R-452A has been introduced during 2015 as a customer option on new truck and trailer refrigeration units. R-404A remains widely available. Activities are ongoing to assess R-744 and other non-flammable (class A1) lower GWP solutions such as R-448A and R-449A. R-513A, R-513B, and R-456A are being considered as future drop-in solutions for HFC-134a. Flammable (A3) and lower flammable (A2L) refrigerant research is continuing, aiming at producing publicly available and technically sound references to support code and standard activities.

- For air-to-air air conditioners and heat pumps, the most substantial recent developments are related to the increased rate of substitution of HCFC-22 and the greater consideration of use of medium and low GWP alternatives. Some manufacturers are adopting HCs and there is also uptake of HFC-32.

- For space heating and water heating heat pumps, legislation on minimum energy efficiency has entered into force in Europe, Japan and the USA, and has decreased the number of air to water heat pumps that can be placed on the market.

- In chillers, after years of research and screening tests, an array of choices is emerging and some commercialisation has begun. Emerging refrigerants are: HCFO-1233zd, HFC-32, R-452B, R-513A, R-514A, HFO-1234yf and HFO-1234ze(E).

- In mobile air conditioners (MACs), the penetration of HFO-1234yf for new vehicles has continued and has spread to many additional models, primarily in non-Article 5 countries, but is still far from complete. In addition, development of R-744 MACs has continued and commercialisation appears imminent. Other alternatives - including hydrocarbons, HFC-152a and additional HFC/HFO blends R-444A and R-445A - have not received much additional consideration and appear unlikely to be chosen for new vehicles in the near future.

- Vapour compression technology has been the primary technology for all R/AC applications in the last 100 years. Technologies that do not employ vapour compression technology are called Not-In-Kind technologies (NIK), of which, during past years, several have been under development. Some studies have classified the development status of those technologies as: (1) most promising (membrane heat pump, thermo-elastic); (2) very promising (evaporative liquid desiccant A/C, magneto-caloric, Vuilleumier heat pump); (3) moderately promising (evaporative cooling, thermo-electric, ground-coupled solid desiccant A/C, absorption heat pump, duplex-Stirling heat pump, thermo-acoustic, adsorption heat pump, thermo-tunneling); and (4) least promising (stand-alone solid desiccant A/C, stand-alone liquid desiccant A/C, ejector heat pump, Brayton heat pump).

## ES4.		Alternatives to refrigeration systems on fishing vessels

- This new chapter responds to the decision request to provide new and updated information, as this is available, related to the availability of alternatives for replacement and retrofit of refrigeration systems in fishing vessels, including in small island countries.

- 70% of the global fishing fleet continues to use HCFC-22 as its main refrigerant. Therefore the main challenge for the industry is to find a feasible transition from HCFC-22 to low-GWP alternatives. Considering that 70% of the global fishing fleet is based in Asia/Pacific, this challenge becomes even more important for Asia/Pacific countries and specifically for the Pacific Island region, whose economy is heavily dependent on their fishing industry. For this reason, particular attention was paid to the situation in this region.

- Based on several parameters (age of vessels, availability of alternatives, technical and economic feasibility of conversions, meeting regulatory requirements of product importer), the transition from HCFC-22 to low-GWP alternatives can be implemented following four different options:

Option 1 – Non-halocarbon refrigerants (i.e., R-717 and R-744);

Option 2 -  Refrigerant replacement with plant adjustments;

Option 3 – Refrigerant drop-in; and

Option 4 -  Maintaining HCFC-22 systems.

## ES5.		Suitability of alternatives under high ambient temperature (HAT) conditions

- Based on comments from Parties on TEAP’s first report to OEWG-37, this revised chapter provides a more balanced discussion (both positive and negative) of the results as well as additional information on the three testing programs for refrigerants under HAT conditions and includes the following changes and additions:

  - Further discussion of the methods for considering the impact of the ambient temperatures on the design of R/AC equipment; and

  - Further information on the reports published for the three projects that tested alternative refrigerants at temperatures above 35°C including tabulated summaries of each of the three projects.

- Chapter 5 updates information on three research projects (where more projects will currently be ongoing) testing alternative refrigerants at HAT conditions and on the design of products using alternatives in new and retrofit applications.

- Results from the three projects, PRAHA, AREP-II, and ORNL, indicate a way forward in the search for efficient low-GWP alternatives for high ambient temperature conditions especially when coupled with a full system redesign. The scope of the research for ORNL and that for the reports from AREP-II analysed here mostly covered soft-optimized testing (i.e., adjusted expansion device or adjusted charge amount). While the PRAHA project included a change of compressors, suppliers did not custom-design those compressors for the particular applications.

- Further improvements are likely through optimizing heat exchangers circuitry for heat transfer properties and proper compressor sizing and selection.

- Full redesign of systems, including new components, will likely be needed to realise systems, using new alternative refrigerants to match or exceed the performance of existing systems in both capacity as well as energy efficiency. When selecting new refrigerants it is important to consider further increases on the current energy efficiency requirements.

- While the commercialization process of refrigerants can take up to ten years, the commercialization of products using these alternatives will take further time.

- In HAT conditions, the cooling load of a conditioned space can be up to three times that for moderate climates. Therefore larger capacity refrigeration systems may be needed, which implies a larger refrigerant charge. Due to the requirements for charge limitation according to certain safety standards, the possible product portfolio suitable for HAT conditions is more limited than for average climate conditions when using the same safety standards.

- Although risk assessment work on flammable refrigerants is an on-going research in some countries, there is a need for a comprehensive risk assessment for A2L and A3 alternatives at installation, servicing and decommissioning at HAT conditions.

## ES6.	  BAU and mitigation demand scenarios for R/AC

- This chapter contains the same scenarios as the TEAP Decision XXVII/4 Task Force Report (March 2016). Based on comments received by TEAP on its report to OEWG-37, this revised chapter also contains the following changes and additions:

  - Consideration of existing regulations as well pending regulations in non-Article 5 Parties and the impact of the latter;

  - Comparison of the demand in non-Article 5 Parties between a BAU scenario with regulations considered (up to 2050) and without regulations considered (up to 2030);

  - A revised table on growth percentages for the various R/AC subsectors, for both the new manufacturing and the total demand (correcting certain percentages of decreasing HCFC demand that were included in the growth percentages in the March 2016 version of the XXVII/4 TF report);

  - Additional information on the production of various HFCs, not only the currently most important ones for the R/AC sector, and a comparison with the global calculated demand for the R/AC sector;

  - Addition of an 18-year manufacturing conversion period for the Article 5 MIT-3 scenario and its impact on total demand; and

  - Related to this chapter, Annex 4 of this report contains updated tables for total, new manufacturing, and servicing demand.

- The revised scenarios in this report include an extension of the timescale used from the year 2030 to 2050 and a consideration of the BAU scenario for non-Article 5 countries that includes the EU F-gas regulation as well as the US HFC regulations for specific sectors and sub-sectors. The mitigation scenarios remain the same as in the September 2015 XXVI/9 report as follows:

  - MIT-3: conversion of new manufacturing by 2020 (completed in non-Article 5 Parties; starting in Article 5 Parties)

  - MIT-4: same as MIT-3 with delayed conversion of stationary AC to 2025

  - MIT-5: conversion of new manufacturing by 2025 (completed in non-Article 5 Parties; starting in Article 5 Parties)

- These scenarios (in principle for the R/AC sector only) were cross-checked against current estimated HFC production data that became available in May 2015 (June and September XXVI/9 Task Force report) and shortly thereafter. Most recent estimates made for the 2015 global production of the four main HFCs are presented in the table below (some revisions were made in this June report); it shows a combined total for the four main HFCs of about 510 ktonnes.

| Chemical | Best estimate for global HFC production in year 2015 (ktonnes) |
| --- | --- |
| HFC-32 | 94 |
| HFC-125 | 130 |
| HFC-134a | 258 |
| HFC-143a | 28 |

- The global calculated bottom-up demand for the R/AC sectors in 2015 amounts to 473 ktonnes (of which 220 ktonnes in non-Article 5, 273 ktonnes in Article 5 Parties). Compared to the total of 510 ktonnes it would imply that the demand from other sectors than R/AC would amount to about 37 ktonnes (this would mainly, but not only, concern HFC-134a, used as a foam blowing agent and used in medical and technical aerosols, as well as some minor use of the other HFCs in other sectors).

- Over the period 2015-2050, the revised BAU scenario shows

  - 250% growth in the demand in tonnes and in tonnes CO2-eq. in non-Article 5 Parties;

  - 700% growth in tonnes and a 800% growth in tonnes CO2-eq. in Article 5 Parties;

  - The increase in total demand for the four main HFCs currently used in R/AC is due primarily to the growth in demand in the stationary AC sub-sector and secondly, to the growth in demand in the commercial refrigeration sub-sector. As mentioned, total global R/AC demand is in the order of 510 ktonnes for the year 2015 for the four main HFCs.

- Delaying the start of conversion: MIT-3 assumes that conversion in all sub-sectors starts in 2020, MIT-5 assumes that conversion starts in 2025. In terms of overall climate impact, the total integrated HFC demand for the R/AC sector in Article 5 Parties over the period 2020-2030 was previously estimated in the different scenarios as follows (assuming a 6 years transition):

  - BAU: 		16,000 Mt CO2 eq.

  - MIT-3:   	  6,500 Mt CO2 eq.; a 60% reduction to BAU (2020-2030)

  - MIT-4:   	  9,800 Mt CO2 eq.; a 40% reduction to BAU (2020-2030)

  - MIT-5:		12,000 Mt CO2 eq.; a 30% reduction to BAU (2020-2030)

- With the scenarios extended to 2050 in this report, the BAU demand for the extended period 2020-2050 increases almost five-fold. In this context, although the differences in reduction between the various mitigation scenarios MIT-3, -4 and -5 remain large, they become proportionately less compared to BAU. Consideration of the intermediate period 2020-2040 may provide a more realistic estimate of the savings that can be realised via the various MIT scenarios in Article 5 Parties. The total integrated HFC demand for the R/AC sector in Article 5 Parties over 2020-2040 is as follows (assuming a 6 years transition):

- BAU: 		42,300 Mt CO2-eq.

- MIT-3:		10,600 Mt CO2-eq.; a 75% reduction to BAU (2020-2040)

- MIT-4:   	15,600 Mt CO2-eq.: a 63% reduction to BAU (2020-2040)

- MIT-5:		18,800 Mt CO2-eq.; a 56% reduction to BAU (2020-2040)

- The MIT-3 and MIT-5 scenarios are given for all Parties, but predominantly reflect demand in Article 5 Parties:

- MIT-3 substantially reduces the high-GWP HFC demand compared to BAU since it addresses all manufacturing conversions in all R/AC sub-sectors as of 2020. As the R/AC manufacturing with high-GWP refrigerants is phased out, the servicing demand becomes dominant. The stationary AC sub-sector is the principal source of the HFC demand.

- MIT-5 delays manufacturing conversion of all sub-sectors, including the rapidly expanding stationary AC sector from 2020 until 2025, so that HFC demand initially rises, but then falls as of the year 2025. Servicing rises substantially as a consequence, and persists for much longer than in MIT-3. MIT-5 shows the impact of persisting servicing needs as a result.

- Conversion period: the longer the conversion period in mitigation scenarios, the greater the climate impacts (see MIT-3 or MIT-5 from 6 to 12 years) and the resulting overall costs in particular because of continuing servicing needs. An 18 years conversion period has been studied for the MIT-3 scenario (costs have not been further addressed compared to what was available in the XXVI/9 TF report). Whereas the 6 and 12 years conversion periods result in a demand decrease starting after 2020-2024, the 18 years conversion period yields a 10% increase in demand first, until the year 2030, then starts to decrease and reaches the 2020 demand value again in the year 2037. For the 18 years conversion period there is still some high GWP servicing demand after 2050. The demand for the period 2020-2050 for a 6 years conversion period is about 15,800 Mt CO2-eq., increases to 20,500 Mt CO2-eq. for a 12 years, and to 27,000 Mt CO2-eq. for an 18 years conversion period. The latter implies a 70% increase in demand compared to demand for a 6 years conversion period.

- For demand in Article 5 Parties, the following is also of importance:

  - Peak values determined for the refrigerant demand increase with later start of conversion. The peak value for MIT-3 in 2020 is about 820 Mt CO2-eq. The peak value for MIT-4 in the year 2023, with conversion of stationary AC starting in 2025, is 25% higher (at 1025 Mt CO2-eq.), whereas the peak value for demand for MIT-5 in the year 2025 is 62% higher than the one for MIT-3 (at 1330 Mt CO2-eq.).

  - For MIT-3, the average decline over a period of 10 years after the peak year is 5.3% per year (from 820 down to 390 Mt CO2-eq. in 2030), for MIT-4 it is 4.5% per year (from 1025 down to 570 Mt CO2-eq. in 2033) and for MIT-5 it is 5.5% per year (from 1330 down to 605 Mt CO2-eq. in 2035).

  - For each separate Article 5 Party the peak (freeze) values will still be in the same years for the various MIT scenarios considered, however, annual reduction percentages achievable thereafter may be significantly different per country.

# 1	Introduction

## 1.1	Terms of Reference for the XXVII/4 Task Force report

Decision XXVII/4 of the Twenty-seventh Meeting of the Parties requested the Technology and Economic Assessment Panel (TEAP) to prepare a draft report for consideration by the Open-ended Working Group (OEWG) at its thirty–seventh meeting, and thereafter an updated report to be submitted to the Twenty Eighth Meeting of the Parties in 2016. In their discussions prior to adoption of this decision, Parties considered a focus primarily on areas where updates to the September 2015 report of the task force of the TEAP addressing the issues of decision XXVI/9, including with regard to information on the availability of alternatives and to extending the mitigation scenarios from the previous report to 2050.

In Decision XXVII/1, paragraph 1, Parties agreed to “work within the Montreal Protocol to an HFC amendment in 2016 by first resolving challenges by generating solutions in the contact group on the feasibility and ways of managing HFCs during Montreal Protocol meetings.” Further, in paragraph 4 of that decision, Parties agreed to “hold in 2016 a series of Open-ended Working Group meetings and other meetings, including an extraordinary meeting of the parties.” Subsequently, in 2016, Parties will hold the thirty-seventh and thirty-eighth OEWG meetings on 4-8 April and 18-21 July, respectively, along with the third Extraordinary Meeting of the Parties 22-23 July. A resumed OEWG-37 meeting has since been planned for 15-16 July. TEAP is providing its response to Decision XXVII/4 in three parts: a first report submitted to OEWG-37 primarily focused on the R/AC sector; this second report now submitted to OEWG-38 addresses comments received at OEWG-37 with the focus remaining on the R/AC sector. Updates related to the other sectors including medical aerosols, non-medical or technical aerosols, and solvents, where updated information is available to the TEAP, as well as responding to comments on the second report from Parties at OEWG-38, as appropriate, will be submitted to the Twenty-eighth Meeting of the Parties (MOP-28). The approach taken by TEAP is further discussed below.

## 1.2	Scope and coverage

The text of Decision XXVII/4 (“Response to the report by the Technology and Economic Assessment Panel on information on alternatives to ozone-depleting substances”), as it relates to this report is as follows:

Decision XXVII/4: Response to the report by the Technology and Economic Assessment Panel on information on alternatives to ozone-depleting substances

Noting with appreciation the September 2015 report of the task force of the Technology and Economic Assessment Panel addressing the issues listed in subparagraphs 1 (a)–(c) of decision XXVI/9,

1.	To request the Technology and Economic Assessment Panel, if necessary in consultation with external experts, to prepare a report for consideration by the Open-ended Working Group at its thirty–seventh meeting, and thereafter an updated report to be submitted to the Twenty-Eighth Meeting of the Parties to the Montreal Protocol on Substances that Deplete the Ozone Layer in 2016, that would:

(a)	Update, where necessary, and provide new information on alternatives to ozone-depleting substances, including not-in-kind alternatives, based on the guidance and assessment criteria provided in subparagraph 1 (a) of decision XXVI/9, and taking into account the most recent findings on the suitability of alternatives under high-ambient temperatures, highlighting in particular:

(i) the availability and market penetration of these alternatives in different regions;

(ii) the availability of alternatives for replacement and retrofit of refrigeration systems in  fishing vessels, including in small island countries;

(iii) new substances in development that could be used as alternatives to ODS and that could become available in the near-future;

(iv) the energy efficiency associated with the use of these alternatives;

(v) The total warming impact and total costs associated with these alternatives and the systems where they are used;

(b)	Update and extend to 2050 all the scenarios in the Decision XXVI/9 report.

## 1.3	Composition of the Task Force and approach

The TEAP established a Task Force to prepare the reports responding to Decision XXVII/4. The updated composition of the Task Force is as follows:

Co-chairs

- Lambert Kuijpers (The Netherlands, Senior Expert member TEAP, RTOC)

- Bella Maranion (USA, co-chair TEAP)

- Roberto Peixoto (Brazil, co-chair RTOC)

Members:

- Radim Cermak (CZ, member RTOC)

- Denis Clodic (France, outside expert)

- Daniel Colbourne (UK, member RTOC)

- Martin Dieryckx (Belgium, member RTOC)

- Piotr Domanski (USA, outside expert (NIST))

- Dave Godwin (USA, member RTOC)

- Bassam Elassaad (Lebanon, member RTOC)

- Armin Hafner (Norway, outside expert)

- Samir Hamed (Jordan, member RTOC)

- D. Mohin Lal (India, member RTOC)

- Richard Lawton (UK, member RTOC)

- Simon Lee (UK, member FTOC)

- Tingxun Li (PR China, member RTOC)

- Richard Lord (USA, outside expert)

- Carloandrea Malvicino (Italy, member RTOC)

- Petter Nekså (Norway, member RTOC)

- Keiichi Ohnishi (Japan, co-chair MCTOC)

- Alaa A. Olama (Egypt, member RTOC)

- Alexander C. Pachai (Denmark, member RTOC)

- Xueqin Pan (France, outside expert)

- Fabio Polonara (Italy, co-chair RTOC)

- Rajan Rajendran (USA, member RTOC)

- Helen Tope (Australia, co-chair MCTOC)

- Dan Verdonik (USA, co-chair HTOC)

- Samuel Yana-Motta (Peru, member RTOC)

- Asbjørn Vonsild (Denmark, member RTOC)

- Jianjun Zhang (PR China, co-chair MCTOC)

- Shiqiu Zhang (PR China, Senior Expert member TEAP)

The structure of the TEAP XXVII/4 Task Force Report was considered by the Task Force and also by TEAP prior to the final formulation of this second report. The factors considered include:

- The relatively short period between the delivery of the final XXVI/9 Report (September 2015) and the preparation of the first report to OEWG-37 and second XXVII/4 Report to be submitted for OEWG-38.

- The similarity of the criteria set out within Decision XXVII/4 and Decision XXVI/9.

- The importance of avoiding too much repetition and bringing focus on updated information from the previous report.

- Recognition that some sectors (specifically refrigeration, air conditioning and foam) have data which allow for the characterisation of a Business-As-Usual (BAU) case and related mitigation scenarios. Recognition that other sectors (specifically fire protection, solvents and medical uses) do not have reliable data from which relevant mitigation scenarios can be derived or for which mitigation scenarios were not derived.

Given the two OEWG meetings, TEAP has taken an approach of providing a response to Decision XXVII/4 as follows:

- For OEWG-37, TEAP provided a first Task Force report focused on R/AC only addressing the relevant paragraphs under paragraph 1(a) of the decision including updates on alternatives, research studies on alternatives under high ambient temperature conditions, and extension of mitigation scenarios to 2050.

- For OEWG-38, TEAP is now providing a second Task Force report that incorporates updates to the R/AC sector information only based on discussions at OEWG-37, and responds to other parts of the decision, including information on alternatives to refrigeration systems on fishing vessels.

- For MOP-28, TEAP will provide a Task Force update report, as appropriate, following discussions during OEWG-38. This will also include update chapters on foam alternatives (and scenarios), fire protection and medical and technical aerosols,  to the extent new information is available.

The chapter layout of this June XXVII/4 Task Force report is as follows:

Executive Summary

Chapter 1 - Introduction

Chapter 2 - Update on the status of refrigerants

Chapter 3 - Update on R/AC alternative refrigerants and technologies

Chapter 4 - Alternatives to refrigeration systems on fishing vessels

Chapter 5 - Suitability of alternatives under high ambient temperature (HAT) conditions

Chapter 6 - BAU and MIT scenarios for A5/non-A5 countries for 1990-2050: R/AC

Annex 1   - Summary of informal discussion on the TEAP Decision XXVII/4 Task Force Report for OEWG-37

Annex 2   - Background information about refrigeration in the fishing industry

Annex 3   - EU (F-gas, MAC Directive), USA (EPA SNAP Program) AND Japan regulatory prohibition

Annex 4  - Updated tables for total, new, manufacturing, and servicing demand

# 2	Update of the status on refrigerants

This chapter essentially contains the same information as the March 2016 version of the XXVII/4 Task Force report, apart from the addition of a subchapter on the definition of “environmentally acceptable” and “environmentally sound” (see 2.9). No new refrigerants or blends have been added to the tables.

## 2.1		Introduction

This chapter in the first report provided updated information on alternatives in the refrigeration and air conditioning sectors since the TEAP Task Force Decision XXVI/9 report, September 2015 (UNEP, 2015) and as requested in Decision XXVII/4. It included:

- A presentation of 80 fluids that have been proposed for testing or are being tested in industry programmes, are pending publication, or have been published in ISO 817 and ASHRAE 34 refrigerant standards since the 2014 RTOC Assessment Report. The majority of these are new mixtures, but traditional fluids and two new refrigerants based on a new molecule are also included.

- A description of how refrigerants are classified in the refrigerant standards, while also noting that with the introduction and potential widespread adaptation of refrigerants which are flammable, have higher toxicity and/or operate at notably higher pressures than the conventional ODS refrigerants or alternative non-flammable HFC refrigerants, as well as increased safety risks of some of low-GWP refrigerants that need to be addressed.

- A discussion of the process of making refrigerants available to the market, including the market mechanisms that decides where a refrigerant will be available.

- A discussion on the methods of assessing the energy efficiency related to the use of a refrigerant.

- A discussion on the discovery of new refrigerants is included. There are alternative refrigerants available today with negligible ODP and lower GWP, but for some applications it can be challenging to reach the same lifetime cost level of the systems while keeping the same performance or to keep the equipment within a reasonable size. The search for new alternative fluids may yield more economical system designs, but the prospects of discovering new, radically different fluids are minimal.

- A discussion of the total warming impact related to refrigerants is discussed, including the difficulty of defining low global warming potential, which plays an essential role in the total warming impact calculation.

## 2.2		Refrigerant data

A total of 80 fluids, new and “old”, are under investigation as alternatives to ODS refrigerants or higher GWP refrigerants (see (UNEP, 2014) for comparison). The fluids have been proposed for testing, are being tested in industry programmes or are pending publication or have been published in ISO 817 (ISO 817:2014) or ASHRAE 34 (ASHRAE 34:2013) since the 2014 RTOC Assessment report (UNEP, 2014).

Of the 80 fluids, 11 are pure substances, of which 10 have been published in ISO 817 or ASHRAE 34, while of the 69 mixtures, 55 have publicly known compositions, but only 17 have been published in the ISO 817 or ASHRAE 34 standards, and of these, 11 were included in the RTOC report (UNEP, 2014).

It is expected that, testing, development and commercialization will decrease the number of viable candidates and that market experience will likely further narrow down the number of viable lower GWP candidates in the future.

For ease of reference, the names of the four largest test programs are provided below.

- AHRI Low-GWP Alternative Refrigerants Evaluation Program (AREP). This project is divided into two phases: Phase I (AREP-I), which is finished, and phase II (AREP-II), which is still ongoing;

- “Promoting low-GWP Refrigerants for Air-Conditioning Sectors in High-Ambient Temperature Countries” (PRAHA);

- “Egyptian Project for Refrigerant Alternatives” (EGYPRA);

- the Oak Ridge National Laboratory (ORNL) “High-Ambient-Temperature Evaluation Program for Low-Global Warming Potential (Low-GWP) Refrigerants”, Phase I (and a new Phase II).

The results of the above programs’ testing of alternatives at high ambient temperature (HAT) conditions are further discussed in Chapter 5. In addition to the programs listed above, several independent or industry-led test campaigns for specific refrigerants are being performed for various applications and climate conditions. Results will be published when available.

The fluids participating in the four programmes named above and the refrigerants proposed under ASHRAE (ASHRAE, 2015), are presented in Table 2-3 for pure fluids and in Table 2-4 for blends with publicly known compositions. For ease of reference, key properties for selected commonly used refrigerants are given in Table 2-5 and Table 2-6.

The fluids which composition is not yet public are (with the safety class in brackets):

- ARC-1 (A1) and LPR1A (A2L) for replacing HCFC-123;

- BRB36 (A1) for replacing HFC-134a;

- ARM-32c (A1), D542HT (A1), DR-91 (A1), and N-20b (A1) for replacing HCFC-22,     R-407C;

- ARM-20b (A2L) for replacing HCFC-22, R-404A, R-407C;

- ARM-32b (A1), D42Yb (A1), D42Yz (A1), and ARM-25a (A2) for replacing R-404A;

- ARM-71a (A2L) and HPR2A (A2L) for replacing R-410A.

Table 2-3: Pure substances proposed under various test programs and in ASHRAE 34

| Refrigerant Designation | Proposed to replace (from AREP phase I) | Safety Class | Participation in AREP program |  | High ambient programmes for HCFC-22 and R-410A alternatives |  |  | Chemical Formula | Chemical Name | Molecular Weight | Boiling Point (°C) | ATEL/ODL (kg/m3) | LFL (kg/m3) | GWP 100 Year (IPCC5) | GWP 100 Year (RTOC) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Phase 1 | Phase 2 | PRAHA | EGYPRA | US DoE |  |  |  |  |  |  |  |  |  |
| HFC-32 | R-404A, R-410A× | A2L | X | X | X | X | X | CH2F2 | Difluoro-methane (methylene fluoride) | 52,0 | −52 | 0,30 | 0,307 | 677 | 704 |  |
| HC-290 | HCFC-22, R-404A, R-407C | A3 | X |  | X | X | X | CH3CH2CH3 | propane | 44,1 | −42 | 0,09 | 0,038 |  | 5 |  |
| HC-600a | HFC-134a | A3 | X |  |  |  |  | CH(CH3)2-CH3 | 2-methyl-propane (isobutane) | 58,1 | −12 | 0,059 | 0,043 |  | ~20 |  |
| R-717 | HCFC-22, R-407C | B2L | X |  |  |  |  | NH3 | ammonia | 17,0 | −33 | 0,000 22 | 0,116 |  |  |  |
| R-744 | R-404A, R-410A | A1 | X |  |  |  |  | CO2 | carbon dioxide | 44,0 | −78◊ | 0,072 | NF | 1 | 1 |  |
| HCFO-1233zd(E) | HCFC-123 | A1 |  | X |  |  |  | CF3CH= CHCl | trans-1-chloro-3,3,3-trifluoro-1-propene | 130,5 | 18,1 | 0 | NF | 1 | 1 |  |
| HFO-1234yf | HFC-134a | A2L | X | X |  |  |  | CF3CF=CH2 | 2,3,3,3-tetrafluoro-1-propene | 114,0 | −29,4 | 0,47 | 0,289 | <1 | <1 |  |
| HFO-1234ze(E) | HFC-134a | A2L | X | X |  |  |  | CF3CH= CHF | trans-1,3,3,3-tetrafluoro-1-propene | 114,0 | −19,0 | 0,28 | 0,303 | <1 | <1 |  |
| HC-1270 | HCFC-22, R-407C | A3 | X |  |  |  |  | CH3CH= CH2 | propene (propylene) | 42,1 | −48 | 0,001 7 | 0,046 |  | 1,8 |  |
| HFO-1336mzz (Z) | HCFC-123 | A1 |  |  |  |  |  | CF3CH=CH-CF3 | cis-1,1,1,4,4,4-hexafluoro-2-butene | 164,1 | 33,4 | 0 | NF | 2 | 2 |  |
| HCC-1130(E)** | HCFC-123 | B2 |  |  |  |  |  | CHCl=CHCl | trans-dichloro-ethene | 96,9 | 47,7 |  |  | <1 | <1 |  |
| Notes: Fluids given with a green background are fluids which were not previously mentioned in the XXVI/9 Task Force report. × HFC-32 was proposed to replace R-404A and R-410A in phase I of the AREP program, but is only proposed to replace R-410A in phase II of same and later projects. ◊ For R-744 the sublimation temperature is given instead of boiling point. Triple point is −56,6 °C at 5,2 bar. **HCC-1130(E) is pending official ASHRAE 34 approval, submitted January 2016. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Table 2-4: Blend refrigerants proposed under various test programs or in ASHRAE 34

| Refrigerant Designation | Refrigerant development name | Proposed to replace (from AREP phase I) | Safety Class | Participation in AREP program |  | High ambient programmes for HCFC-22 and R-410A alternatives |  |  | Composition | Molecular Weight | Bubble point/dew or Normal boiling point (°C) | GWP 100 Year (IPCC5) | GWP 100 Year (RTOC) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Phase 1 | Phase 2 | PRAHA | EGYPRA | US DoE |  |  |  |  |  |
| R-514A** | XP30 | HCFC-123 | B1 |  |  |  |  |  | R-1336mzz(Z)/1130 (E) (74,7/25,3) | 139,6 |  | 1,7 | 1,7 |
| — | ARM-41a | HFC-134a | A1 | X |  |  |  |  | R-134a/1234yf/32 (63/31/6) | 99,5 |  | 860 | 900 |
| R-513A | XP10 | HFC-134a | A1 | X | X |  |  |  | R-1234yf/134a (56/44) | 108,4 | −29,2 | 570 | 600 |
| — | N-13a | HFC-134a | A1 | X |  |  |  |  | R-134a/1234ze(E)/1234yf (42/40/18) | 108,7 |  | 550 | 570 |
| R-450A | N-13b | HFC-134a | A1 | X | X |  |  |  | R-1234ze(E)/134a (58/42) | 108,7 | –23,4/ –22,8 | 550 | 570 |
| R-515A** | HDR-115 | HFC-134a | A1 |  |  |  |  |  | R-1234ze(E)/227ea (88/12) | 118,7 | -19,2 | 400 | 380 |
| R-513B* |  | HFC-134a | A1 |  |  |  |  |  | R-1234yf/134a (58,5/41,5) | 108,7 | −29,9 | 540 | 560 |
| — | D-4Y | HFC-134a | A1 | X | X |  |  |  | R-1234yf/134a (60/40) | 108,9 |  | 520 | 540 |
| — | AC5X | HFC-134a | A1 | X | X |  |  |  | R-1234ze(E)/134a/32 (53/40/7) | 100,9 |  | 570 | 590 |
| — | ARM-42a | HFC-134a | A2L | X | X |  |  |  | R-1234yf/152a/134a (82/11/7) | 104,8 |  | 110 | 110 |
| R-444A | AC5 | HFC-134a | A2L | X | X |  |  |  | R-1234ze(E)/32/152a (83/12/5) | 96,7 | –34,3/ –24,3 | 89 | 93 |
| R-445A | AC6 | HFC- 134a | A2L |  |  |  |  |  | R-744/134a/1234ze(E) (6/9/85) | 103,1 | –50,3/ –23,5 | 120 | 120 |
| — | R290/R600a | HFC-134a | A3 | X |  |  |  |  | R-600a/290 (60/40) | 51,6 |  |  | 14 |
| R-456A** |  | HFC-134a | A1 |  |  |  |  |  | R-32/134a/1234ze(E) (6/45/49) | 101,4 | -31,1/ -25,7 | 630 | 650 |
| R-407G |  | HFC-134a | A1 |  |  |  |  |  | R-32/125/134a (2,5/2,5/95,0) | 100,0 | -29,1/ -27,2 | 1 300 | 1 400 |
| — | LTR4X | HCFC-22, R-407C | A1 | X | X |  |  |  | R-1234ze(E)/32/125/134a (31/28/25/16) | 85,1 |  | 1 200 | 1 300 |
| — | N-20 | HCFC-22, R-407C | A1 | X | X |  |  |  | R-134a/1234ze(E)/1234yf/ 32/125 (31,5/30/13,5/12,5/12,5) | 96,7 |  | 890 | 950 |
| — | D52Y | HCFC-22, R-407C | A2L | X | X |  |  |  | R-1234yf/125/32 (60/25/15) | 97,8 |  | 890 | 970 |
| — | L-20 | HCFC-22, R-407C | A2L | X |  |  |  |  | R-32/1234ze(E)/152a (45/35/20) | 67,8 |  | 330 | 350 |
| — | LTR6A | HCFC-22, R-407C | A2L | X | X |  |  |  | R-1234ze(E)/32/744 (63/30/7) | 77,6 |  | 200 | 210 |
| R-444B | L-20a | HCFC-22, R-407C | A2L |  | X | X | X | X | R-32/1234ze(E)/152a (41,5/48,5/10) | 72,8 | –44,6/ –34,9 | 300 | 310 |
| — | ARM-32a | HCFC-22, R-404A, R-407C | A1 | X |  |  |  |  | R-125/32/134a/1234yf (30/25/25/20) | 86,9 |  | 1 400 | 1 600 |
| R-442A |  | HCFC-22, R-404A, R-407C | A1 |  | X |  |  |  | R-32/125/134a/152a/227ea (31,0/31,0/30,0/3,0/5,0) | 81,8 | –46,5/ –39,9 | 1 800 | 1 900 |
| R-449B |  | HCFC-22, R-404A, R-407C | A1 |  |  |  |  |  | R-32/125/1234yf/134a (25,2/24,3/23,2/27,3) | 86,4 | −46,1/ −40,2 | 1 300 | 1 400 |
| R-449C* | DR-93 | HCFC-22, R-407C | A1 |  |  |  |  | X | R-32/125/1234yf/134a (20/20/31/29) | 90,3 | −45,5/−38,5 | 1 100 | 1 200 |
| R-453A | RS-70 | HCFC-22, R-407C | A1 |  |  |  |  |  | R-32/125/134a/227ea/600/ 601a (20,0/20,0/53,8/5,0/0,6/0,6) | 88,8 | -42,2/ -35,0 | 1 600 | 1 700 |
| R-407H* |  | HCFC-22, R-407C | A1 |  |  |  |  |  | R-32/125/134a (32,5/15,0/52,5) | 79,1 | -44,6/ -37,6 | 1 400 | 1 500 |
| R-449A | DR-33 (XP40) | R-404A | A1 | X | X |  |  |  | R-32/125/1234yf/134a (24,3/24,7/25,3/25,7) | 87,2 | –46,0/ –39,9 | 1 300 | 1 400 |
| — | N-40a | R-404A | A1 | X |  |  |  |  | R-32/125/134a/1234ze(E)/ 1234yf (25/25/21/20/9) | 87 |  | 1 200 | 1 300 |
| — | N-40b | R-404A | A1 | X |  |  |  |  | R-1234yf/32/125/134a (30/25/25/20) | 87,1 |  | 1 200 | 1 300 |
| R-452A | DR-34 (XP44) | R-404A | A1 |  | X |  |  |  | R-1234yf/32/125 (30/11/59) | 103,5 | −47,0/ −43,2 | 1 900 | 2 100 |
| R-452C** | ARM-35 | R-404A | A1 |  |  |  |  |  | R-32/125/1234yf (12,5/61,0/26,5) | 101,9 | -47,8/ -44,4 | 2 000 | 2 200 |
| R-448A | N-40c | R-404A | A1 |  | X |  |  |  | R-32/125/1234yf/134a/ 1234ze(E) (26,0/26,0/20,0/21,0/7,0) | 86,3 | –45,9/ –39,8 | 1 300 | 1 400 |
| — | R32/R134a | R-404A | A2L | X |  |  |  |  | R-32/134a (50/50) | 68,9 |  | 990 | 1 000 |
| — | ARM-31a | R-404A | A2L | X |  |  |  |  | R-1234yf/32/134a (51/28/21) | 83,9 |  | 460 | 480 |
| — | L-40 | R-404A | A2L | X | X |  |  |  | R-32/1234ze(E)/1234yf/ 152a (40/30/20/10) | 73,6 |  | 290 | 300 |
| R-454A | DR-7◊ | R-404A | A2L | X | X |  |  |  | R-1234yf/32 (65/35) | 80,5 | −48,4/ −41,6 | 240 | 250 |
| R-454C* | DR-3 | R-404A | A2L |  | X | X | X | X | R-1234yf/32 (78,5/21,5) | 90,8 | −45,8/ −38,0 | 150 | 150 |
| R-454A | D2Y-65 | R-404A | A2L | X | X |  |  |  | R-1234yf/32 (65/35) | 80,5 | −48,4/ −41,6 | 240 | 250 |
| R-457A** | ARM-20a | R-404A | A2L |  |  |  |  |  | R-32/1234yf/152a (18/70/12) | 87,6 |  | 140 | 150 |
| — | ARM-30a | R-404A | A2L | X |  |  |  |  | R-1234yf/32 (71/29) | 84,7 |  | 200 | 200 |
| R-455A | HDR-110 | R-404A | A2L |  | X |  |  |  | R-32/1234yf/744 (21,5/75,5/3) | 87,5 | -51,6/ -39,1 | 150 | 150 |
| — | R32/R134a | R-410A | A2L | X |  |  |  |  | R-32/134a (95/5) | 53,3 |  | 710 | 740 |
| — | R32/R152a | R-410A | A2L | X |  |  |  |  | R-32/152a (95/5) | 52,6 |  | 650 | 680 |
| — | DR-5 | R-410A | A2L | X |  |  |  |  | R-32/1234yf (72,5/27,5) | 61,2 |  | 490 | 510 |
| — | L-41a | R-410A | A2L | X |  |  |  |  | R-32/1234yf/1234ze(E) (73/15/12) | 61 |  | 490 | 510 |
| — | L-41b | R-410A | A2L | X |  |  |  |  | R-32/1234ze(E) (73/27) | 61 |  | 490 | 510 |
| — | ARM-70a | R-410A | A2L | X |  |  |  |  | R-32/1234yf/134a (50/40/10) | 70,9 |  | 470 | 490 |
| — | HPR1D | R-410A | A2L | X | X |  |  |  | R-32/1234ze(E)/744 (60/34/6) | 63 |  | 410 | 420 |
| — | D2Y-60 | R-410A | A2L | X | X |  |  |  | R-1234yf/32 (60/40) | 77,2 |  | 270 | 280 |
| R-454B | DR-5A | R-410A | A2L |  | X | X | X | X | R-32/1234yf (68,9/31,1) | 62,6 | −50,9/ −50,0 | 470 | 490 |
| R-452B** | DR-55 (XL55) | R-410A | A2L |  |  |  |  | X | R-32/1234yf/125 (67/26/7) | 63,5 | -50,9/-50,0 | 680 | 710 |
| R-446A | L-41-1 | R-410A | A2L |  | X |  |  |  | R-32/1234ze(E)/600 (68,0/29,0/3,0) | 62 | –49,4/ –44,0 | 460 | 480 |
| R-447A | L-41-2 | R-410A | A2L |  | X | X | X | X | R-32/125/1234ze(E) (68,0/3,5/28,5) | 63 | –49,3/ –44,2 | 570 | 600 |
| R-447B** | L-41z | R-410A | A2L |  |  |  |  |  | R-32/125/1234ze(E) (68,0/8,0/24,0) | 63,1 | –50,3/ –46,2 | 710 | 750 |
| Notes: Fluids given with a green background are fluids which were not mentioned in the XXVI/9 Task Force report. * Indicates refrigerants pending official ASHRAE 34 approval, submitted June 2015. ** Indicates refrigerants pending official ASHRAE 34 approval, submitted January 2016. ◊ DR-7 has changed nominal composition slightly from originally R-1234yf/32 (64/36) to R-1234yf/32 (65/35). |  |  |  |  |  |  |  |  |  |  |  |  |  |

Table 2-5:  Currently commonly used pure substances for reference

| Refrigerant Designation | Safety Class | Chemical Formula | Chemical Name | Molecular Weight | Boiling Point (°C) | ATEL/ODL (kg/m3) | Atmospheric Lifetime (Years) | Radiative Efficiency (W/m/ ppm) |  | GWP 100 Year (IPCC5) | GWP 100 Year (RTOC) | ODP |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| HCFC-22 | A1 | CHClF2 | chlorodifluoromethane | 86,5 | -41 | 0,21 | 12 | 0,21 |  | 1 760 | 1 780 | 0,034 |
| HCFC-123 | B1 | CHCl2CF3 | 2,2-dichloro-1,1,1-trifluoroethane | 152,9 | 27 | 0,057 | 1,3 | 0,15 |  | 79 | 79 | 0,01 |
| HFC-134a | A1 | CH2FCF3 | 1,1,1,2-tetrafluoroethane | 102,0 | -26 | 0,21 | 14 | 0,16 |  | 1 300 | 1 360 |  |
| HC-290 | A3 | CH3CH2CH3 | propane | 44,1 | −42 | 0,09 | 12,5 days |  |  |  | 5 |  |
| HC-600a | A3 | CH(CH3)2-CH3 | 2-methyl-propane (isobutane) | 58,1 | −12 | 0,059 | 6,0 days |  |  |  | ~20 |  |
| R-717 | B2L | NH3 | ammonia | 17,0 | −33 | 0,000 22 |  |  |  |  |  |  |
| R-744 | A1 | CO2 | carbon dioxide | 44,0 | −78◊ | 0,072 |  |  |  | 1 | 1 |  |

Table 2-6:  Currently commonly used blend refrigerants for reference

| Refrigerant Designation | Safety Class | Refrigerant Composition (Mass %) | Molecular Weight | Bubble / Dew or Normal Boiling Point (°C) | ATEL/ODL (kg/m3) | GWP 100 Year (IPCC) | GWP 100 Year (RTOC) | ODP |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| R-404A | A1 | R-125/143a/134a (44,0/52,0/4,0) | 97,6 | -46,6/-45,8 | 0,52 | 3 900 | 4 200 |  |
| R-407A | A1 | R-32/125/134a (20,0/40,0/40,0) | 90,1 | -45,2/-38,7 | 0,31 | 1 900 | 2 100 |  |
| R-407C | A1 | R-32/125/134a (23,0/25,0/52,0) | 86,2 | -43,8/-36,7 | 0,29 | 1 600 | 1 700 |  |
| R-407F | A1 | R-32/125/134a (30,0/30,0/40,0) | 82,1 | -46,1/-39,7 | 0,32 | 1 700 | 1 800 |  |
| R-410A | A1 | R-32/125 (50,0/50,0) | 72,6 | -51,6/-51,5 | 0,42 | 1 900 | 2 100 |  |
| R-507A | A1 | R-125/143a (50,0/50,0) | 98,9 | -47,1/-47,1 | 0,53 | 4 000 | 4 300 |  |

As in the previous Decision XXVI/9 Task Force report, the data sources for Tables 2-3 through 2-6 are as follows:

- “GWP (RTOC)” values are taken from the 2014 RTOC report (UNEP, 2014) where available (they are based on (WMO, 2014)); where not available the value is calculated based on values for pure fluids from the 2014 RTOC report (UNEP, 2014).

- “GWP (IPCC5)” values are taken from the IPCC AR5 report (IPCC, 2014) for pure fluids; for mixtures values are calculated based values for pure fluids from the IPCC AR5 report (IPCC, 2014).

- For Tables 2-3 and 2-4, refrigerant designations, safety classes and compositions are taken from the AHRI AREP program where available, otherwise from ASHRAE 34 public review (ASHRAE, 2015).

- All other data in Tables 2-3 through 2-6 are taken from the 2014 RTOC report (UNEP, 2014).

## 2.3		Refrigerant classification and standards

Refrigerants are classified by the refrigerant standard ISO 817 and ASHRAE 34 into 8 classes depending on toxicity and flammability, for instance: A1, A2L, A3 or B2L. The first, a letter A or B, indicates the toxicity of the fluid:

- A, lower chronic toxicity, have an occupational exposure limit of 400 ppm or greater

- B, higher chronic toxicity, have an occupational exposure limit of less than 400 ppm

The suffix 1, 2L, 2 or 3 indicates the flammability:

- 1, no flame propagation, measured at 60 °C

- 2L, lower flammability, burning velocity not higher than 10cm/s, energy of combustion below 19 MJ/kg and not flammable below 3.5 % volume concentration.

- 2, flammable, energy of combustion below 19 MJ/kg and not flammable below 3.5 % volume concentration.

- 3, higher flammability.

These safety classes are used by the system safety standards, such as ISO 5149, IEC 60335-2-24, IEC 60335-2-40, IEC 60335-2-89, EN378 and ASHRAE 15.

With the introduction and potentially wide use of refrigerants that are flammable, have higher toxicity and/or operate at notably higher pressures than the conventional ODS refrigerants or alternative non-flammable HFC refrigerants, consideration of safety matters has become more important. Accordingly, more attention is presently being paid to the requirements of safety standards and regulations that directly relate to refrigerants that exhibit these characteristics.

For instance, the safety standards sets upper limits on how much refrigerant charge is allowed in a refrigerant circuit, primarily depending on the safety class, location of the equipment, and on the type of people who have access to the equipment; the amount of charge is related to the cooling or heating capacity of the equipment. Using a wall mounted split A/C unit in a 30 m2 room as an example, the safety standard, in this case IEC 6335-2-40, allows 0.413 kg of HC-290 per refrigeration circuit, while for HFC-32 it allows 5.6 kg charge, due to the different flammability characteristics of the substances. Clearly a more than 10 times higher charge allows higher cooling capacity with HFC-32. It also requires a higher level of optimising to account for the low charge limitation when using HC-290.

## 2.4		Likelihood of new molecules and new radically different blends

There are alternative refrigerants available today with negligible ODP and (lower or) low GWP, but for some applications it can be challenging to reach the same lifetime cost level of the systems while keeping the same performance. The search for new alternative fluids may yield more economical system designs, but as will be explained below, the prospects of discovering new, radically different fluids are minimal.

The alternative refrigerants must have suitable thermodynamic properties, which determine the efficiency and capacity of the system. In addition, they need to satisfy several other criteria, such as zero ODP, low GWP, low toxicity, stability in the system, materials compatibility, acceptable cost, and, if possible, non-flammability, lower flammability or low-risk due to flammability. These requirements are difficult to balance.

The list of proposed R-410A and HCFC-22 replacement candidates includes single-component refrigerants (HFC-32, HC-290, HC-1270, R-717, R-744). The list also includes blends, which, in addition to the listed single-component candidates, comprise the so-called hydrofluoroolefins (unsaturated HFCs) such as HFO-1234yf and HFO-1234ze(E), along with traditional (saturated) HFC refrigerants to achieve the desired attributes of the blend, e.g., low GWP, lower flammability, or lubricant compatibility. Through ongoing evaluation studies, the performance potentials of these alternatives are being established.

Significant efforts have been done in the past to find new fluids. A recent study (McLinden, 2015) started with a database of over 150 million chemicals, screening the more than 56,000 small molecules and finding none of them ideal. It can be concluded from the study that the prospects of discovering new chemicals that would offer better performance than the fluids currently known are minimal.

## 2.5		Road to availability of alternative refrigerants

As discussed in the Task Force Decision XXVI/9 Report (UNEP, 2015), developing a new fluid is a process where uncertainties are addressed, both regarding what is technically feasible and what can be accepted by the market. It is a process structured in discrete steps, where some are visible to the industry. The commercialisation of a new molecule is complicated and can take significant time, while for mixtures consisting of existing molecules the commercialisation is much faster. Once the fluid is launched in the market, the availability is largely controlled by where there is a market need.

The technical uncertainty includes how to produce the fluid, and whether the preferred properties can be attained. The market uncertainty includes uncertainty about what properties the customer prefers, and what fluids the competitors will market.

The development process requires a series of investments, such as researching the toxicity of candidate fluids, or doing field tests at potential customers with a candidate fluid. The investment pattern is similar from fluid to fluid, and companies therefore manage the process with a state-gate process (Cooper, 1988). The state-gate process uses a “gate” or decision point placed just in-front of each major investment, so that management can decide whether or not to accept the next investment or stop the development project. While the exact gates are not visible from outside the company, some of the steps will be visible in the market. Examples of such steps could be:

- Research, possibly in collaboration with a few selected system builders;

- Fluid (with a research acronym) released for small scale testing in industry test programs;

- R-number applied for through ASHRAE 34 (or ISO 817) and is normally accepted;

- Testing in the market to see whether the market is interested in larger capacities;

- Broad market launch (large scale production set-up);

- Submission and acceptance under pertinent government regulations (e.g., REACH or SNAP);

- Market adoption, where the market actually starts using the refrigerant in larger quantities.

Within the context of development of low GWP refrigerants, one of the most important incentives is the occurrence of relevant legislation that hinders competing fluids or opens pathways for new fluids and creates some measure of certainty for investments into the market.

The investment sizes and time needed for each step for new molecules (pure refrigerants) are much larger and longer than for refrigerant mixtures. Research and toxicity evaluation are expensive in the early phases, and the production set in the later stages, are expensive for new molecules. While for new mixtures, the major uncertainty is related to the market, and the large investments are primarily on research, especially market research, to find a composition which matches the needs of the customers as well as possible, and on the market launch with investments in marketing.

This means that the commercialisation of a new fluid can take 10 years, while for mixtures the commercialisation takes closer to 5 years. An issue for the new mixtures is that many contain one of the two new molecules, HFO-1234yf or HFO-1234ze(E), which may have had only limited production until recently.

Once the fluid is launched in the market, companies will invest where they see the greatest market potential. There is a limit to how many different refrigerants customers, service companies, and sales channels in a given market will accept. Market shares obtained in the early phase tends to be relatively easy to sustain, which is why companies can be very picky about where they launch a product. Although current availability to the markets and market launch plans for specific fluids are proprietary information, there is however the general rule of thumb that new fluids will be available where a sufficiently large share of users request it.

Two examples of the step from commercial productions to market launch in specific markets are as follows:

- Commercial production of HFO-1234ze(E) started at the end 2014 in manufacturing plants in the US. It is now already commercially used in chillers by companies in the US, EU and Japan; besides and it is also applied in one-component foam and some aerosol propellant applications. Within two years after the start of commercial production, it is currently commercially available in the US, Europe and most of Asia.

- Commercial production of HCFO-1233zd(E) started by mid-year of 2014 in plants located in the USA. It is used in low pressure centrifugal chillers, which have been released in Europe, the Middle East and other 50 Hz markets; and it is also used in foam applications as a replacement for HFC-245fa. Within two years after the start of commercial production, it is currently commercially available in the US, Europe and most of Asia.

## 2.6		Energy efficiency in relation to refrigerants

Assessing the energy efficiency associated with a refrigerant is a complicated process, and the results depend on the approach taken. Energy efficiency of refrigeration systems is, in addition to the refrigerant choice, related to system configuration, component efficiencies, operating conditions, operating profile, system capacity, and system hardware, among others, which makes a consistent comparison difficult in many instances.

One approach is to start with a target refrigerant and use a system architecture suitable for this specific refrigerant, while comparing it with a reference system for the refrigerant to be replaced.

Another approach is to screen for alternative refrigerants suitable for a given system architecture. The common methods for determining the efficiency in this case can be placed into one of three categories:

- theoretical and semi-theoretical cycle simulations

- detailed equipment simulation models, and

- laboratory tests of the equipment.

In a refrigerant selection process, great reliance is placed on cycle simulations for selecting best candidate fluids for further examination either by equipment simulation models or tests of actual equipment.

Most often, cycle simulations employ a refrigerant’s thermodynamic properties along with fixed values for temperatures inside the system and fixed compressor isentropic efficiency. These models are popular among refrigeration practitioners because they are simple in principle and easy to use. However, the shortcomings to be kept in mind include not taking into account the heat transfer properties and pressure drops in a system. Detailed simulation models do not have this shortcoming (Domanski, 2006).

Laboratory tests provide the ‘most trusted’ information about performance of a refrigerant in a given system. It must be recognized that tests of a new refrigerant in a system optimized for a different refrigerant do not demonstrate the performance potential of the refrigerant tested (Abdelaziz, 2015). In addition to system ‘soft-optimization’, which includes adjustment of the refrigerant charge and expansion device, ‘hard optimization’ is necessary, which includes, among others, optimization of the compressor (including the size), refrigerant circuitry in the evaporator and condenser, and the overall system balance.

Hard optimization is a rather involved process. Usually, it is most effectively implemented by concurrent detailed simulations and extensive testing. It can be particularly complicated with blends of significant temperature glide, which offer special challenges and opportunities in heat exchanger design. Hence, overall system design and successful optimization play a significant role in achieving the refrigerant performance potential in a commercialized product. In practice the hard optimization is also limited by the cost of the system, as the success in the market depends on a cost/performance trade-off. In addition, it is also constrained by commercial availability (e.g., manufacturing ability) for certain components, such as availability of preferred compressor displacement, heat exchanger dimensioning and capability to produce preferred circuitry.

To illustrate the difficulties of assessing the energy efficiency associated with a refrigerant, consider the tests under high ambient temperature conditions described in Chapter 5 of this report:

- Testing temperatures differs from test program to test program.

- Obviously no single temperature can accurately match a real geographical location, so the results do not relate directly to the actual energy consumption in a real situation.

- The units (including technologies) used for testing varied within the same test programs.

- In some tests only the refrigerant is changed, in others the oil or even the compressor are changed.

- Differences in test protocols further contributed to differences in results, for example, adjusting the expansion device, adjusting the charge, or adjusting compressor displacement to match compressor and heat exchanger capacity.

- The cost/performance ratio is an important factor (see above) but it is difficult to analyse in the test programs as other long term parameters need to be considered.

## 2.7		Climate impact related to refrigerants

There are a number of difficulties in assessing the climate impact including the difficulties of obtaining reliable and accurate data on system leakage rates and determining the carbon emissions generated, now and in the future, and in producing the energy necessary to power the R/AC and HP system.

Climate impact related to refrigerants consists of direct and indirect contributions. The direct contribution is a function of a refrigerant’s GWP, charge amount and leakage rates (annual, catastrophic, and during servicing and decommissioning) from the air-conditioning and refrigeration (R/AC and HP) equipment. The indirect contribution accounts for the CO2-equivalent emissions generated during the production of the energy consumed by the R/AC and HP equipment, its operating characteristics and the emissions factor of the local electricity production. The relative importance of the direct and indirect contributions will depend on the type of system. Systems that are “more leaky”, e.g., automotive vehicle air conditioning, typically have larger relative contributions from direct warming than would “tighter systems”, e.g., hermetically sealed chiller systems, although this can be offset for systems that have much shorter operating periods or where power is supplied from a source with low carbon content.

There are several metrics that measure the total emissions from a system. Most common are Total Equivalent Warming Impact (TEWI) and Life Cycle Climate Performance (LCCP) which attempts to quantify the total global warming impact by evaluating the R/AC and heat pump systems during their lifetime from “cradle to grave” (IIR, 2016). Sometimes, a TEWI calculation may be simplified by neglecting broader effects including manufacture of the refrigerant and equipment, and disposal of the refrigerant and equipment after decommissioning. More in-depth analyses not usually performed also look at the emissions associated with the production and disposal of the equipment, e.g., including the mining and recycling of the metal used to manufacture compressors, heat exchangers, and other components.

To summarize, the most important factors determining the climate impact are:

- The GWP of the refrigerant multiplied with the amount leaking from the system, this is the direct contribution.

- Energy consumption of the system multiplied with the amount of CO2 generated per unit of energy, this is part of the indirect contribution.

The uncertainty on energy consumption and leakage makes determining the total climate impact difficult.

## 2.8	The GWP classification issue

To minimize direct climate impact, a lower GWP refrigerant can be used. The RTOC 2014 Assessment Report included a taxonomy of GWP values, including what constitutes high, medium, and low GWP (again given in Table 2-7 below). This taxonomy is based on fixed GWP values.

Table 2-7 defines “low” as smaller than 300 and “high” as more than 1000. There are sources that define low as lower than 25, as lower than 100, or as lower than 150 (which results from the 2006 EU MAC directive). It will be clear that “high”, “medium” and “low” are qualifiers, related to a scale, and that a number definition of these levels would be a non-technical choice. This also because it is somehow related to what is acceptable in specific applications.

Table 2-7:   Classification of 100 year GWP levels

| 100 Year GWP | Classification |
| --- | --- |
| < 30 | Ultra-low or Negligible |
| < 100 | Very low |
| < 300 | Low |
| 300-1000 | Medium |
| > 1000 | High |
| > 3000 | Very high |
| > 10000 | Ultra-high |

For instance, there is a relationship between the pressure, the GWP and the flammability of a refrigerant, as illustrated in Table 2-8, which is also from the RTOC 2014 Assessment Report (UNEP, 2014). The trend can be described as “the higher the pressure, the higher the minimum GWP which is needed for fluids to be non-flammable”. The exception to this relationship is R-717 and R-744, which do not fit this pattern. Therefore, what could be an “acceptable” GWP for a high pressure fluid replacing R-410A may not be “acceptable” for a low pressure fluid replacing HFC-134a. But this does not relate to a definition of a GWP classification in an absolute sense.

Table 2-8:  100 year GWPs for synthetic refrigerants and hydrocarbons

| Safety Class | Range of GWP for Alternatives to |  |  |
| --- | --- | --- | --- |
|  | HFC-134a | HCFC-22, R-404A, R-407C, and R-507A | R-410A |
| A1 | 540 – 900 | 950 – 1600 |  |
| A2L | ≤ 110 | 200 – 970 | 280 – 740 |
| A3 | 14 – 20 | 1,8 – 5 |  |

The two refrigerants that do not fit this pattern, both being in the category with ultra-low GWP, are R-717 and R-744. These are for many applications considered as alternatives to the current higher GWP HFCs. Though toxic in principle, R-744 is a safety class A1 refrigerant, while R-717 is in class B2L.

## 2.9		Environmentally sustainable and environmentally sound

The alternatives described under “low” or “lower” GWP here aim at satisfying a criterion of “environmentally sustainable” or “environmentally sound” (as this classification was used in Decision XXVI/9, taken in 2014).

“By environmental sustainability we mean meeting current human needs without undermining the capacity of the environment to provide for those needs over the long term.” (http://www.unmillenniumproject.org/documents/EnvironSust_summary.pdf).

None of the substances proposed as refrigerants are without potentially adverse impacts to the environment if the emissions are large enough (with the exception of water and air, neither of which can be widely applied). A good example is R-744 (CO2) which has no ODP and a very low GWP, however its emissions related to energy production are the primary contributor to global warming. What the environment and humanity is able or willing to handle is a policy decision, and so is the fraction of the environmental load allowed to be related to refrigerant emissions. One option to consider might be setting certain limits on direct refrigerant emissions relative to the IPCC 2050 scenarios. One could propose that a maximum of 1% of total GHG emissions could be an acceptable contribution of refrigerants and foam blowing agents. However, even with this type of policy approach the question remains of how emissions should be distributed between various application sectors  within this very “broad” industry. Further, determining how much GHGs (HFCs) could be produced, and over what time frame, and how banks of these chemicals would be addressed such that the emissions through 2050 met this criterion, would involve establishing highly uncertain assumptions (e.g., leak rates) which could be very different between those various applications.

The following definition for ”environmentally sound” is often used: “An environmentally sound product or manufacturing process is a product or process that, from beginning to end, is in essential harmony with its environment and the associated ecological factors”

(http://www.businessdictionary.com/definition/environmentally-sound.html)

Article 10, paragraph (c) of the Kyoto Protocol (as decided in 1997) reiterated that all Parties shall: “co-operate in the promotion of effective modalities for the development, application and diffusion of, and take all practicable steps to promote, facilitate and finance, as appropriate, the transfer of, or access to, environmentally sound technologies, know-how, practices and processes pertinent to climate change, in particular to developing countries, including the formulation of policies and programmes for the effective transfer of environmentally sound technologies that are publicly owned or in the public domain and the creation of an enabling environment for the private sector, to promote and enhance the transfer of, and access to, environmentally sound technologies.”

The IPCC in its AR5 report (IPCC, 2014) describes barriers for the spread of environmentally sound technologies (ESTs), as follows: “The spread of proven environmentally sound technologies that would diffuse through commercial transactions may be limited because of existing barriers. Barriers to the transfer of environmentally sound technologies arise at each stage of the process. These vary according to the specific context, for example from sector to sector and can manifest themselves differently in developed countries, developing countries and countries with economies in transition.” The IPCC report provides an extensive overview of the most important barriers in developed, developing and transition economies that could impede the transfer of environmentally sound technologies to mitigate and adapt to climate change. Governments can promote technology transfer by reducing these barriers.

## 2.10		References

Abdelaziz, 2015	Abdelaziz, O. et al., 2015. Alternative Refrigerant Evaluation for High-Ambient-Temperature Environments:R-22 and R 410A Alternative for Mini-Split Air Conditioners, ORNL/TM-1015/536

AHRI, 2015	AHRI Low GWP Alternative Refrigerants Evaluation Program, (Low-GWP AREP), Participants Handbook, 2015

ASHRAE 15-2013	ANSI/ASHRAE, 2015. Standard 15-2013 with addendum a, Designation and Safety Classification of Refrigerants American Society of Heating, Refrigerating, and Air-Conditioning Engineers (ASHRAE), Atlanta, GA, USA

ASHRAE 34-2013	ANSI/ASHRAE, 2015. Standard 34-2013 with addenda a to x, Designation and Safety Classification of Refrigerants American Society of Heating, Refrigerating, and Air-Conditioning Engineers (ASHRAE), Atlanta, GA, USA

ASHRAE, 2015	Online Standards Actions & Public Review Drafts, https://osr.ashrae.org/default.aspx (documents only available during the review period)

Abdelaziz, 2015	Abdelaziz, O. et al., 2015. Alternative Refrigerant Evaluation for High-Ambient-Temperature Environments:R-22 and R 410A Alternative for Mini-Split Air Conditioners, ORNL/TM-1015/536

Cooper, 1988	Cooper, R. G., 1988. The New Product Process: A Decision Guide for Management. Journal of Marketing Management 2:238-255

Domanski, 2006	Domanski, P.A., Yashar, D., 2006. Comparable Performance Evaluation of HC and HFC Refrigerants in an Optimized System, 7th IIR Gustav Lorentzen Conference on Natural Working Fluids, Trondheim, Norway, May 28-31.

EN 378 	EN 378-1:2008+A2:2012, EN 378-2:2008+A2:2012, EN 378-3:2008+A1:2012. EN 378-4:2008+A1:2012, Refrigeration Systems and Heat Pumps – Safety and Environmental Requirements

IEC 60335-2-24 	IEC 60335-2-24:2010, Specification for safety of household and similar electrical appliances. Particular requirements for refrigerating appliances, ice-cream appliances and ice-makers

IEC 60335-2-40 	IEC 60335-2-40:2003+A13:2012, Specification for safety of household and similar electrical appliances. Safety. Particular requirements for electrical heat pumps air-conditioners, and dehumidifiers

IEC 60335-2-89 	IEC 60335-2-89:2010, Specification for safety of household and similar electrical appliances. Safety. Particular requirements for commercial refrigerating appliances with an incorporated or remote refrigerant condensing unit or compressor

IIR, 2016	The LCCP Working Group, International Institute of Refrigeration (IIR), 2016. Guideline for Life Cycle Climate Performance.

IPCC, 2014		Myhre, G., D. Shindell, F.-M. Bréon, W. Collins, J. Fuglestvedt, J. Huang, D. Koch, J.-F. Lamarque, D. Lee, B. Mendoza, T. Nakajima, A. Robock, G. Stephens, T. Takemura and H. Zhang, 2013. Anthropogenic and Natural Radiative Forcing. In: Climate Change 2013: The Physical Science Basis. Contribution of Working Group I to the Fifth Assessment Report of the Intergovernmental Panel on Climate Change (Stocker, T.F., D. Qin, G.-K. Plattner, M. Tignor, S.K. Allen, J. Boschung, A. Nauels, Y. Xia, V. Bex and P.M. Midgley (eds.)]. Cambridge University Press, Cambridge, United Kingdom and New York, NY, USA

ISO 817:2014	ISO 817: 2014. Refrigerants — Designation and safety classification. International Organization for Standardization (ISO)

ISO 5149	ISO 5149: 2014, Refrigerating systems and heat pumps — Safety and environmental requirements. International Organization for Standardization (ISO)

McLinden 2015	McLinden, M. O., Kazakov, A. F., Brown, J. S. & Domanski, P. A. Hitting the bounds of chemistry:  Limits and tradeoffs for low-GWP refrigerants. 24th Int. Congress of Refrig. (Yokohama, Japan, August 16-22, 2015).

UNEP, 2014		UNEP Nairobi, Ozone Secretariat, 2015. Report of the Refrigeration, Air Conditioning and Heat Pumps Technical Option Committee, 2014 Assessment. ISBN: 978-9966-076-09-0.

UNEP, 2015	UNEP, Update Report of the XXVI/9 TEAP Task Force, September 2015, ISBN 978-9966-076-14-4

WMO, 2014		Assessment for Decision-makers, Scientific Assessment of Ozone Depletion: 2014. WMO Global Ozone Research and Monitoring Project - Report No. 56, published online September 2014, in print January 2015, ISBN 978-9966-076-00-7.

# 3	Update on R/AC alternative refrigerants and technologies

This is a new chapter in this second version of the Task Force report (comparable to the updated chapter in the XXVI/9 TF report, September 2015). It presents information on alternative refrigerants for the various types of R/AC equipment using them as well as information on (NIK-Not In Kind) alternative technologies (see section 3.9). It also gives the latest developments for the use of efficient CO2 technology (see section 3.10) and elaborates on the use of standards with regard to the safe use of refrigerants in the R/AC industry (see section 3.11).

## 3.1		Domestic Appliances

HC-600a and HFC-134a continue to be the primary refrigerant options for production of new equipment. It is projected that, by 2020, about 75% of new refrigerator production will use HC-600a, most of the rest will use HFC-134a, and a small share may apply unsaturated HFC refrigerants such as HFO-1234yf.

Globally, the activity undertaken so far on HFO-1234yf in domestic refrigerator applications remains very limited and is not being pursued with high priority, due to cost implications. The use of HFO-1234yf in a domestic freezer has been tested as a proof of concept.

The Association of Home Appliance Manufactures (AHAM) of North America has recently announced a voluntary goal to phase down HFC-134a in household refrigerators and freezers after 2024. It is not yet clear whether manufacturers will choose HC-600a (class A2) or HFO-1234yf (class A2L) as both are flammable and still have to adhere to current and emerging safety and energy efficiency standards.

In the proposed USA Significant New Alternatives Policy (SNAP) listing of 18 April 2016, HFC-134a in domestic appliances is listed as undesirable as of 1/1/2021. The EU F-gas regulation 517/2014 prohibits the use of HFC-134a in domestic appliances as of 1/1/2015. This implies that the change to a low GWP refrigerant (defined as GWP <150 in 517/2014), away from HFC-134a, is a real issue here.

The heat pump clothes (laundry) dryer (HPCD) sales using HFC-134a are rapidly growing in the EU. HPCDs using R-407C and HC-290 have also been introduced. New research with R-744 shows significant efficiency gain may be possible. Alternative refrigerant solutions that are being explored include HC-600a and low GWP HFOs.

## 3.2		Commercial Refrigeration

# While the F-gas regulation 517/2014 is now effective in Europe, in the United States, the Environmental Protection Agency (EPA), as already mentioned above, published a final rule for change of status of refrigerants in several applications under its SNAP program. Of significance were three changes of status: (1) for supermarket systems, (2)  for condensing units and (3) one for self-contained coolers and freezers. In all of these applications, the high GWP HFC blend R-404A is not allowed in new equipment starting in January 1, 2017 for supermarkets, January 1, 2018 for condensing units and January 1, 2019 or 2020 for certain self-contained systems. Canada has signalled its intention to do something similar, and the US state of California is looking to the European F-gas regulation for its regulation. These are examples of governments that have started down the path of not allowing high GWP HFC refrigerants or HFC based blends in new equipment.

# Lower GWP refrigerants and HFC blends (both class A1 and class A2L) are also being approved for use in various equipment types. The recent impact of these developments is summarized below for various refrigerants as relevant to commercial refrigeration equipment.

# In supermarkets, blends such as R-448A, R-449-A, R-449B, R-450A, and R-513A are now beginning to grow in use, starting with Europe and the US. Component manufacturers (compressors, valves, controls etc.,) are releasing new products and approving existing products for use with these new refrigerants which range from half to a third of the GWP of the refrigerants that they are replacing.

# The same holds true for condensing units and self-contained equipment. In the self-contained equipment category, early trials with HFO-1234yf and HFO-1234ze(E) have begun as well. The use of R-407A and R-407F (at approximately half the GWP of R-404A and with similar performance in systems) continues to grow in many parts of the world.

Refrigerants such as R-744 are increasingly being used in supermarket systems worldwide – both in cascaded systems (R-744 for low temperature cascaded with a second refrigerant like HFC-134a or similar and R-717 in limited cases) and in transcritical systems. Transcritical systems are being researched extensively to reduce their energy penalty at high ambient conditions through the use of component and system technologies such as ejector, adiabatic condensing, sub-cooling and parallel compression. R-744 is also beginning to see its use in walk-in applications with condensing units. Self-contained systems are increasingly moving from R-404A, HCFC-22 and HFC-134a to HC-290 or R-744. Charge limits continue to limit the size of the equipment possible with the hydrocarbon refrigerant.

## 3.3		Industrial Systems

In the time since the release of the 2014 RTOC Assessment report, a number of overarching trends have been identified and are expected to be included in the 2018 Assessment report.

The biggest trend in industrial refrigeration, which also forms an extensive challenge, is the constant focus on refrigerant charge reduction. Another big trend in the market is the heat pump market development. Industrial heat pumps use heat that is considered waste in other parts of production processes. An example is the dairy sector, where milk is both cooled and heated in different sequences. The pasteurization process requires temperatures around 70 to 80°C. Different technologies are used to achieve these temperatures.

For industrial processes, high temperature heat pumps are required, with temperatures to be produced of up to about 100 °C, sometimes even up to 180°C. Water Vapour Recompression (VRC, process recovering low heat steam at low pressure and compressing it to a high pressure and high temperature) is gaining a lot of attention.

District energy concepts (District Heating combined with District Cooling, «DC») are growing all over the world. In Europe, the two countries where the DC concept is most applied are France and Sweden. There is now more emphasis on applying DC in the Middle East post the 2014 assessment since it has the largest DC growth potential in the world. Recently the Multilateral Fund Executive Committee approved demonstration projects in the area. Implementing agencies UNIDO/UNEP are preparing demonstration projects in Egypt, Kuwait and Colombia to help establish “New Technologies”, legislation and benefits of DC for these areas. District heating and DC are growing in many markets, including in Article 5 Parties. DC can be driven by vapour compression or absorption (which fits into NIK) but in any case it requires significant investments in infrastructure. This is the reason why they are economically viable only when new buildings or new buildings networks are involved.

In some Parties, industrial refrigeration systems have been widely based on HCFC-22. Also in Article 5 Parties, the trend is now to abandon it and look for drop-in alternatives or for new refrigerant solutions.

## 3.4		Transport refrigeration

R-452A has been introduced during 2015 as a customer option on new truck and trailer refrigeration units (it is a blend consisting of HFC-32, HFC-125 and HFO-1234yf). R-404A continues to be offered as well for its wide availability. R-452A has similar cooling capacity, fuel efficiency, reliability and refrigerant charge as R-404A, but it offers a 45% GWP reduction. The features supporting R-452A in transport refrigeration include non-flammability and low compressor discharge temperatures. By January 2016, one manufacturer has sold 1500+ units with R-452A already. The close property match of

R-452A to R-404A gives customers the option to retrofit their existing fleets. The conversion does not require component changes and it can be carried out in the field during the life of the product.

In addition, activities are ongoing to assess R-744 and other non-flammable (A1) lower GWP solutions such as R-448A and R-449A. R-513A, R-513B, and R-456A are being considered as future drop-in solutions for HFC-134a that is utilized in some refrigerated vans and a large number of marine containers. These blends have approximately 50% of the GWP of HFC-134a. R&D is ongoing, but no products have been released so far based on these refrigerants.

Flammable (A3) and lower flammable (A2L) refrigerant research has continued, aiming at producing publicly available and technically sound references to support code and standard activities with regard to transport systems. König and Bararu (2014) have shown that frequency of hazard and probabilities of fatalities for the global reefer container fleet would be below 10-6 (one in a million) if adequate design changes were in place and best practice guidelines were established. In February 2016, the first meeting took place to develop the International Organisation for Standardisation (ISO) 20854 safety standard for refrigerating systems using flammable (A2) and lower flammable (A2L) refrigerants in marine containers. The feasibility of using HC-290 in trucks has been demonstrated in a demo unit in South Africa and was presented at the MOP-27 in Dubai in 2015. The benefits are an improved energy performance and lower life cycle CO2 emissions. The project included a risk assessment, careful components selection, and leak simulation tests.

An energy optimization of a cryogenic system has entered a commercial testing phase in the United Kingdom (UK). The system uses liquid nitrogen to provide cooling through its expansion and to power a Dearman engine supplying a vapour compression cycle. A second generation machine is being developed but this has not yet reached a commercially viable stage.

A UK supermarket chain continues carrying out trials of an R-744 refrigerated trailer since 2013. They revealed that they have subsequently acquired a second R-744 trailer that can operate at different temperatures and this will be joined by a third in 2016. Since 2012, companies shipping and leasing reefer containers have continued to trial R-744 units from the same manufacturer.

The German and French railways have continued to look at air cycle systems as alternatives to vapour compression systems. Deutsche Bahn (DB) has equipped the first car of an Intercity Express (ICE) train in March 2015 while Société Nationale des Chemins de Fer (SNCF) has set up a 24-months demonstration program in a regional train.

## 3.5		Air-to-air air conditioners and heat pumps

Air conditioners, including reversible air heating heat pumps (generally defined as “reversible heat pumps”), range in size from 1 kW to 750 kW although the majority are less than 70 kW. The most populous are non-ducted single splits, which are produced in excess of 100 million units per year. Whilst nearly all air conditioners manufactured prior to 2000 used HCFC-22, all products sold within non-Article 5 Parties now use non-ODS refrigerants, albeit largely without the use of low-GWP alternatives. For most products, R-410A is used. Whilst the production of air conditioners using HCFC-22 remains the dominant option within Article 5 Parties there is a substantial shift in many countries to move to HFCs and HCs, approximately one half of all units produced globally use non-ODP refrigerants. Nevertheless, the majority of the installed unit population still uses HCFC-22; an estimated two-thirds of a billion HCFC-22 air conditioners are operating worldwide, representing approximately one million tonnes of HCFC-22.

The most substantial recent developments are related to the increased rate of substitution of HCFC-22 and the greater consideration of use of medium and low GWP alternatives. Previously, medium and low GWP alternatives were not being given major consideration (except HCs such as HC-290) whereas now additional manufacturers are adopting HCs and there is also uptake of HFC-32, especially in Japan where in 2014 100% of residential split air conditioner production was switched to HFC-32. Several enterprises – in Japan, and recently in other Parties as well, – are promoting and selling air conditioners using HFC-32 outside of Japan. Many enterprises are also considering and evaluating new HFC/HFO blends, such as mixtures of various compositions of HFC-32, HFC-125, HFC-134a, HFO-1234yf and HFO-1234ze(E). Broad testing has been carried out of these mixtures within various collaborative industry projects and the results are being made available on a regular basis. Whilst R-744 remains to be applied in larger types of systems within more temperature climates, there has not been any significant shift in increasing adoption of the technology.

China has completed the conversion of 18 production lines to HC-290 as part of their HPMP and portable units are being sold widely. In India, at least one plant has produced several hundred thousand HC-290 split air conditioners. There is also additional information relating to different alternatives performance under high ambient conditions. Nevertheless, some enterprises within the Middle East still see R-407C and HFC-134a as favourable alternatives to HCFC-22.

In light of the fact that almost all medium and low GWP alternatives are flammable there has been significant progress with the development of new requirements for safety standards (particularly for increasing refrigerant charge size), with working groups addressing A2, A2L and A3 refrigerants at both IEC and ISO level. Due to the complexities of the process it is unclear by when amendments will be finally published.

## 3.6		Water heating heat pumps

In Europe, Japan and the US, the legislation on minimum energy efficiency for space heating and water heating heat pumps became active and has limited the number of air to water heat pumps that can be placed on the market.

For space heating heat pumps in the EU, the minimum energy efficiency was set as a primary energy efficiency based on seasonal efficiency, placed in an average European climate with a design temperature at -10°C, including standby losses. From September 2015 on, all space heating heat pumps shall have a primary energy efficiency of 100%. For low temperature space heating heat pumps it shall be 115%. This results in a seasonal coefficient of performance (SCOP) of respectively 2.5 and 2.875. From September 2017 onwards, the values shall be 110% (SCOP of 2.75) and 125% (SCOP of 3.125). The seasonal efficiency is based on a specific temperature pattern and includes standby energy losses. For water heating heat pumps the requirements are less restrictive except for larger systems where the requirements will have restrictions as of September 2018. For the moment, there is no drastic impact on the refrigerant currently used.

HFC-32 has been just introduced by one manufacturer in Japan as the refrigerant for water heating systems (mainly R-744 products are sold in the market). Unlike R-744, which can produce hot water with temperatures up to 90°C, the temperature of the water is limited to 65°C. The main purpose is to offer a cost competitive and high energy efficiency solution for families with lifestyles suited to operations of this system.

## 3.7		Chillers

The components, refrigeration cycles used, systems, and application of chillers remains largely unchanged from the 2014 RTOC Assessment Report or since 1980 for that matter with exception of increased use of variable-speed drives. Vapour compression technology dominates all chiller types, and there has been little progress towards commercialisation of magnetic refrigeration based chillers and other not-in-kind technologies. However, absorption chillers are, and will continue to be, part of the global mix of chillers. In all regions, there is a demand for higher performance chillers and the systems that use them, at both full and partial load. Some manufacturers are offering newly designed compressors, have expanded the use of variable speed drives and permanent magnet motors, and are using more sophisticated control systems. Manufacturers, consumers, and regulators alike have had an ongoing interest in low GWP refrigerants with high thermodynamic efficiency. The slow movement to new refrigerants reflects the high cost of product development and tooling changes, as well as the uncertainty in the supply of new refrigerants by chemical producers who also face huge investments and regulatory hurdles. None-the-less, chiller manufacturers seem to be gravitating to lower GWP alternative refrigerants, and have introduced a number of new products that use them.

The 2104 RTOC Assessment Report gave a complete discussion of the trade-offs and research efforts associated with use of lower GWP refrigerants. As noted in the report, in order to be acceptable, new refrigerants should result in products with energy efficiencies that are equal to or better than the refrigerants replaced. Secondly, the global warming effects from chillers are dominated by the energy-related component from their power consumption. Total Equivalent Warming Impact (TEWI) and Life Cycle Climate Performance (LCCP) models typically show that more than 95% of the climate effect is due to energy consumption. The direct global warming effects from refrigerant emissions are significantly smaller since direct emissions have been significantly reduced in recent years through lower charge systems, low-leak designs, manufacturing and testing improvements, and improved service practices.

Chillers have traditionally used an array of refrigerants due to the economics associated with high performance compressors as well as physical size and manufacturing constraints over the range of capacities provided by chillers. Table 9-1 of the 2014 RTOC Assessment Report gave a discussion and complete listing of all chiller types by size, compressor type, and refrigerants used.

After years of research and screening tests, an array of choices is emerging. Some commercialization has started and recent new product introductions indicate that a change has started (shown in Table 3-1).

Table 3-1 Emerging refrigerants used in Chillers

| Product | Refrigerants presently in use | Emerging refrigerants |
| --- | --- | --- |
| Large chillers with centrifugal compressors using low pressure refrigerants | CFC-112 HCFC-123 1 HFC-245fa | HCFO-1233zd(E) R-514A |
| Large chillers with centrifugal compressors using medium pressure refrigerants | CFC-122 HFC-134a | R-513A HFO-1234yf HFO-1234ze(E) |
| Mid-size chillers with positive displacement (screw) compressors | CFC-122 HFC-134a | R-513A HFO-1234yf3 HFO-1234ze(E)3 |
| Small chillers with positive displacement (scroll or recip) compressors | HCFC-222 R-407C R-410A | HFC-323 R-452B3 |

- Phase-out in new equipment in 2020

- Phased out but may still be used for servicing in Article 5 Parties

- Classified as A2L refrigerant (lower flammable)

The emerging refrigerants may not be the final selections. With high efficiency as a primary customer requirement, new product introductions will use refrigerants that likely preserve or improve thermodynamic efficiency with significantly reduced GWPs. A number of refrigerants are listed as safety class 2L (flammable with flame propagation speeds of 10 cm/s or less). Some Parties, notably the U.S., have not yet implemented the necessary product standards and code changes to use these refrigerants in the occupied space or in large machinery rooms without the burdensome requirements of safety class 2 or 3, highly flammable refrigerants. Even with codes and standards changes, some additional application cost may be expected. Taken together with generally higher refrigerant costs, this means that the cost of new chillers with lower GWP refrigerants is likely higher. Manufacturers typically pass along additional costs, and therefore the price is likely higher, which typically will dampen the demand as long as the existing product is not discontinued.

Regulation is taking a leading role in mandating the adoption of new refrigerants with lower GWPs. There is continued pressure for the use of lower GWP refrigerants in all Parties and industry is responding. For example, AHRI (the manufacturer’s trade association in the US) and NRDC (the National Resources Defense Council, Washington, D.C.) recently agreed to discontinue sale of chillers using higher GWP refrigerants HFC-134a, R-410A and R-407C by 1/1/2025. This agreement is consistent with the emerging refrigerants listed in Table 3-1. The agreement also provides support to the US EPA’s proposal to ban all 3 refrigerants from new production chillers, although the EPA proposed timeline is somewhat quicker. The time to 2025 will allow manufacturers to complete the design and implementation of full product lines, and work on cost reductions. At the same time, refrigerant producers will need to increase capacity to meet demand, and put products into the product service infrastructure. Ideally, as the product changes occur, major disruptions will be avoided.

One can also not overlook the role that zero or near-zero GWP refrigerants such as R-717, R-718, and HC-290, and absorption chillers may play. As noted in the 2014 RTOC Assessment Report, these alternatives have been available for some time, and new choices may emerge. It is impossible to predict the market mix that may emerge, especially in view of future government regulations or incentives.

As far as drop-in alternatives or retrofits are concerned, it is too early to tell if manufacturers will offer retrofit packages for use in upgrading existing chillers with the emerging lower GWP refrigerants. While technically possible, it would not be likely for several reasons. First, all compressor types are optimized for the specific refrigerant used. Substituting a different refrigerant usually results in a loss of capacity, efficiency or both. Second, the pressure ratio for fixed displacement compressors may limit the ability of the compressor to reach the appropriate pressure rise when a different refrigerant is used. A similar phenomenon is found in centrifugal compressors when changing refrigerants, but may be overcome with a change in impellers or speed when a variable speed drive is used. Third, many of the emerging refrigerants are safety class 2L. Use of a safety class 2L refrigerant to replace a safety class 1 refrigerant may require significant changes to meet the building codes and standards, as well as product standards (such as UL, listing to a product standard). These things taken together would likely discourage retrofits.

## 3.8		Vehicle air conditioning

Since the 2014 RTOC Assessment Report, no new alternatives have been introduced in light-duty mobile air conditioners (MACs). The penetration of HFO-1234yf for new vehicles has continued and has spread to many additional models, primarily in non-Article 5 Parties, but is still far from complete. HFC-134a continues to be used in the majority of new vehicles, especially in vehicles used in Article 5 Parties. Regulations and announcements of such - including the MAC Directive of 2006 in the EU, credit system and model year 2021 HFC-134a phase-out in the US, the Canadian consideration of bans and HFC phasedowns, and the Japanese target GWP of 150 by 2023, - continues to be primary factors influencing this trend. In addition, development of R-744 MACs has continued and appears imminent, with announcements from Mercedes-Benz to use it in new S-class and E-class models for the EU beginning in 2017, and indications that Audi A8 and Volkswagen Phaeton models will also use R-744 in 2017.

Other alternatives that were discussed in the 2014 RTOC Assessment report, - including hydrocarbons, HFC-152a and additional HFC/HFO blends R-444A and R-445A, - have not received much additional consideration and appear unlikely to be chosen for new vehicles in the near future.

The trend in electrified drivetrains continues, with hybrids and battery-electric vehicles capturing more of the market. This is important in terms of refrigerant as these vehicles will increase the desire for heat pump (heating and cooling) systems in lieu of cooling-only systems. More advanced designs integrating battery and/or electronics cooling with the passenger comfort system are likely to be introduced.

Buses still rely primarily on HFC-134a and R-407C for passenger comfort. Some vehicles using R-744 are operating, and their use, while currently low (perhaps about 20 buses), is increasing but is limited by the availability of open-type compressors. The trend to hybrid electric buses will allow hermetic or semi-hermetic compressors, making the use of R-744 more likely.

Heavy Duty trucks still rely on HFC-134a for driver comfort. Some versions are likely to introduce HFO-1234yf soon.

## 3.9		Not-In-Kind technologies

This chapter looks into technologies that do not employ vapour compression technology. They are called Not-In –Kind-Technologies (NIK). Vapour compression technology has been the dominant technology for all R/AC applications in the last 100 years. Nevertheless, during past years several other technologies have been developed. The development status of those technologies can be classified as:

- R&D status

- Emerging technology

- Commercially available

Recently, the U.S. Department of Energy (U.S. DoE, 2014) developed a study to characterize and evaluate alternatives to vapour-compression technology to serve future residential and commercial HVAC applications. Provided below are some of the main aspects of this study.

NIK technology classifications are divided into three groups according to their particular driving energy. Those are:

- Thermally driven.

- Electro- mechanically driven.

- Solid State driven.

Seventeen NIK technologies from these 3 groups were compared in the study to a baseline vapour compression technology, considering the following criteria:

- Energy savings potential.

- Non-energy benefits.

- Cost/complexity.

- Heating and cooling capabilities.

- Development status.

- Market barriers.

Based on these criteria they were classified as i) most promising, ii) very promising, iii) moderately promising, and iv) least promising:

- Most promising: membrane heat pump, thermo-elastic;

- Very promising: evaporative liquid desiccant A/C, magneto-caloric, Vuilleumier heat pump;

- Moderately promising: evaporative cooling, thermo-electric, ground-coupled solid desiccant A/C, absorption heat pump, duplex-Stirling heat pump, thermo-acoustic, adsorption heat pump, thermo-tunneling;

- Least promising: stand-alone solid desiccant A/C, stand-alone liquid desiccant A/C, ejector heat pump, Brayton heat pump.

The present status, the development of prototypes and equipment and the expected technical progress of some NIK technologies are as follows:

Thermo-elastic and Membrane Technologies:

A one TR (3.52 kW) window air conditioner prototype that operates on thermo-elastic technology is undergoing testing. In another facility, one manufacturer developed a one TR (3.52 kW) prototype space- conditioning system that operates on Membrane Heat Pump technology using this two stage (latent and sensible) technology. The manufacturer predicts an EER of 26 Btu/Whr or greater.

Absorption, Evaporative and Evaporative Liquid Desiccant Technologies:

Absorption heat pumps are commercially available and have an inherent advantage since they can operate on low heat energy exergy thus saving on precious peak electric power. Evaporative cooling has always been an attractive alternative in Hot-Dry conditions, although Indirect/Direct evaporative cooling can be used in both dry and humid hot conditions, its water consumption rates can be a risk in arid conditions. Evaporative Liquid Desiccant technology, a R&D technology, also consumes water and careful selection is needed in regions where water is scarce.

Ground coupled Solid Desiccant AC Magneto-caloric and Vuilleumier Heat Pump technologies.

Ground coupled Solid Desiccant AC is also a R&D technology and uses (low exergy) thermal energy. Magneto-caloric and Vuilleumier Heat Pump technologies are both in the emerging phase and are promising technologies.

## 3.10		Developments of CO2 technology

Applying CO2 (R-744) as a working fluid is common in hot water and industrial heat pumps, light commercial beverage cooling and especially in supermarket refrigeration.

Due to the thermodynamic properties of CO2, throttling losses compared to conventional low-pressure fluids are significantly higher, particularly at elevated heat rejection temperatures common at higher ambient temperatures where the energy efficiency of the CO2 units is lower.

Introducing an internal heat exchanger can help to reduce the throttling losses. In addition, utilising the kinetic energy of the fluid flowing from the high- to the low-pressure side can save compressor work instead of dissipating it in the throttling process. Two apparatuses are able to perform such work recovery, expanders and ejectors.

Expanders uses the throttling energy to assist the compressor and are comparable with compressors with respect to cost and complexity.

Ejectors are more comparable to expansion devices, however, they use the expansion of the high-pressure fluid to entrain and compress a low-pressure fluid by means of momentum transfer between the two steams inside the ejector without moving parts. Ejectors are suitable for dedicated applications due to their high robustness, reliability and potential low cost.

As reported by Elbel and Lawrence (2016), the work recovery efficiency of CO2 ejectors is generally in the range of 20-30%, which means that 20-30% of the normally dissipated expansion work is applied to unload the compressor by pre-compressing the suction stream from suction inlet pressure (evaporator outlet) to the separator pressure (compressor inlet). Unloading the compressor is not the only benefit of an ejector, using it to simultaneously pump additional liquid through the evaporators, i.e. overfeeding them, avoids dry-out and improves the evaporator and system performance significantly. This increases the required suction pressure of the compressor twice, firstly due to the elevated evaporation temperature (flooded evaporation) and the pre-compression of the evaporator outlet fluid.

For commercial refrigeration applications, as in supermarkets, ejector systems enabling continuously flooded evaporator operation are commercially available. There are more than 40 ejector supported CO2 installations around the globe. The first pilot systems applying additional compressor unloading by pre-compressing of medium temperature vapour (from chilled food display cabinets) are successfully operated for several years in Switzerland (Schönenberger et al. 2014).

The multi-ejector is an add-on enhancement technology increasing the energy efficiency at high ambient temperatures to a state of the art CO2 booster system with parallel compression. The parallel compression booster system represents a development step towards higher energy efficiency compared to the traditional booster systems with flash gas by-pass.

Based on the experimental investigations in laboratories and field tests of the CO2 supermarket systems, a seasonal energy efficiency improvement of 10% is obtained between a CO2 booster and a similar system with parallel compression. At high ambient temperatures, another 20% improvement is achievable when adding the multi-ejector technology to a well-designed CO2 parallel compression system. Global supermarket chains, operating CO2 ejector supported supermarkets in Spain, have measured an annual energy saving of 25% compared to the previous HFC unit installed prior to the remodelling of the supermarket.

Utilization of heat recovery for space heating (where needed) and hot water production is an important part of the refrigeration systems and can be done with CO2 without any large extra effort.

CO2 ejector technology is under development for other applications such as industrial or commercial cold storage refrigeration systems, transport refrigeration systems, industrial heat pump applications, chillers, etc.

## 3.11 		Standards in the R/AC industry

For the refrigeration, air-conditioning and heat-pump industry the two most important standardisation organisations for international standards are the International Organization for Standardisation (ISO) and the International Electro-technical Commission (IEC). In some cases, standards from nationally based organisations will be more recognised in the field (e.g., ASHRAE, UL and SAE in the United States). In these cases, efforts may be made to harmonise with ISO and IEC standards as appropriate.

ISO has published two standards of high relevance to the topic of refrigerants: (1) “ISO 817 Refrigerants - Designation and safety classification” and (2) “ISO 5149 Refrigerating systems and heat pumps - Safety and environmental requirements”. ISO 5149 is the primary standard for larger systems. IEC has published relevant application specific standards as parts of the standard “IEC 60335 Household and similar electrical appliances – Safety”, for instance “IEC 60335-2-40 Household and similar electrical appliances - Safety - Part 2-40: Particular requirements for electrical heat pumps, air-conditioners and dehumidifiers”. The IEC application standards are typically used for factory build systems, while the ISO 5149 is typically used for larger systems.

The safety standards covers topics such as:

- Refrigerant safety: Definitions and charge limits and definitions.

- Construction: Approval of components, piping, joints and assemblies, pressure testing and tightness requirements, safety valves and switches, setting and selection, avoidance of ignition sources for flammables.

- Installation: Machine rooms, other installation sites, ventilation.

- Maintenance: Safe practices, avoid leaking refrigerants

Some of these topics, especially the charge limits, have profound influence on which refrigerants are considered safe to use in what applications.

The text of a standard is produced by a Working Group, a sub-committee of the Technical Committee of either ISO or IEC responsible for all standards related to refrigerating systems safety. In shorthand this is ISO/TC86/SC1 or IEC/TC61D/SC61. The technical committee members are nominated representatives of national standards bodies (NSB) and the committee business is conducted by ballot, with votes cast by the head of delegation from each country on behalf of their NSB. In contrast, the members of a WG are nominated experts who do not represent a country or NSB and who do not need to be members of the TC. The WG strives to meet face-to-face, and participation of experts in the standardisation working groups is typically sponsored by the employer of the expert. Membership of the Technical Committee is open to representatives of all member countries (ISO has 161 members, while IEC has 83 members and associated members).

The international standards preparation processes comprise several defined stages requiring alternate input from NSBs and Working Group members. A committee draft is prepared by the WG and circulated to NSBs for comment. The comments received are resolved to the best of the WG’s ability in discussion, within a consensus process and the resultant draft standard is sent to the NSB’s for vote. The rules for voting are complex but clearly defined. The standard is only accepted if several criteria are met. In some cases, particularly if a large number of comments are received to the draft standard, the text will go back to the working group for review and will then be recirculated as a second draft. Once the text has been refined, the standard will be reissued as a final draft for vote by the NSB’s. If the votes meet the criteria then the text will proceed to publication.

## 3.12 		References

Elbel and Lawrence, 2016     Review of recent developments in advanced ejector technology. 2016. Int. J. Refrigeration, Volume 62, February 2016, pp. 1-18, ISSN 0140-7007

Schönenberger et al., 2014	Experience with ejectors implemented in a R-744 booster system operating in a supermarket. 2014. 11th IIR GL Conference, Hangzhou, China (paper 19)

U.S. DoE, 2014 	Energy Savings Potential and RD&D Opportunities for Non-Vapor-Compression HVAC Technologies

# 4 	Alternatives to refrigeration systems on fishing vessels

This new chapter responds to the decision request to provide new and updated information, as this is available, related to “the availability of alternatives for replacement and retrofit of refrigeration systems in fishing vessels, including in small island countries.” Related to this chapter, Annex 2 contains additional background information on refrigeration systems in the fishing industry (with a special focus on the situation of the Pacific Islands region).

## 4.1	Introduction

In order to respond to the following question asked within the Decision XXVII/4 of the Twenty-seventh Meeting of the Parties:

(a)	Update, where necessary, and provide new information on alternatives to ozone-depleting substances, including not-in-kind alternatives, based on the guidance and assessment criteria provided in subparagraph 1 (a) of decision XXVI/9, and taking into account the most recent findings on the suitability of alternatives under high-ambient temperatures, highlighting in particular :

(ii)	the availability of alternatives for replacement and retrofit of refrigeration systems in fishing vessels, including in small island countries;

a Working Group was established within the TEAP Decision XXVII/4 Task Force.

As their first action, the members of the Working Group, aiming at clarifying the problems being experienced by the fishing industry, compiled a questionnaire to be circulated to Parties in order that an understanding of their needs could be ascertained. Responses to the questionnaire as well as further investigation of worldwide fishing practices, refrigeration systems and techniques employed were considered by the Working Group in the development of this chapter (see Annex 2 for a broader description).

## 4.2		Considerations and options for replacement and retrofit of refrigeration systems in fishing vessels

As a summary of the analysis performed on the world fishing industry, with a particular attention on the situation in the Pacific Islands region, the following are important considerations of the options for replacement and retrofit of refrigeration systems on fishing vessels:

- 70% of the global fishing fleet continues to use HCFC-22 as its main refrigerant. Therefore the main challenge for the industry is to find a feasible transition from HCFC-22 to low-GWP alternatives.

- Considering that 70% of the global fishing fleet is based in Asia/Pacific, this challenge becomes even more important for Asia/Pacific Parties and specifically for the Pacific Island region, whose economy is heavily dependent on their fishing industry.

- Based on several parameters (age of vessels, availability of alternatives, technical and economic feasibility of conversions, meeting regulatory requirements of product importer), the transition from HCFC-22 to low-GWP alternatives can be implemented following four different options as further discussed in the following sections, with rating provided according to the degree of financial, technical and regulatory risk, and in Annex 2:

  - Option 1 – Non-halocarbon refrigerants

  - Option 2 -  Refrigerant replacement with plant adjustments

  - Option 3 – Refrigerant drop-in

  - Option 4 -  Maintaining HCFC-22

4.2.1 Option 1 – Non-halocarbon refrigerants (R-717 and R-744)

Current technology present several interesting options, catering for almost all the industry requirements. Systems with ammonia (R-717), carbon dioxide (R-744) or ammonia/carbon dioxide cascade cover almost all the possible applications. Due to the costs and modifications involved when transiting from an HCFC-22 plant to a non-halocarbon refrigerant, R-717 options cannot be considered a viable solution for the replacement or retrofit of refrigeration plants on existing vessels considered here. However, their choice is probably the right one when new ships are considered or when rebuilding can be accepted. Running an ammonia plant requires skilled personnel. R-744 option can be a good solution also for existing vessels as demonstrated by recent experiences. Cost of systems for conversion to R-717 and R-744 options compete with HFC systems in the markets where they so far have been sold.

|  | Financial considerations |  | Technology risk (Complexity and performance) | Regulatory and environmental risk (10 years horizon) |
| --- | --- | --- | --- | --- |
|  | Capital investment | Operating expenses |  |  |
| Option 1 – Non-halocarbon refrigerants |  |  |  |  |
| R-717 system | Medium | Medium | High | Nil |
|  | Requires new ship with separate machine room or rebuilding | Potential improvement in efficiency. Require competence, but inexpensive refrigerant | Highly complex relative to on-board capabilities. Additional safety risk of ammonia (lower flammable and toxic). Training required in new markets | No environmental policy risk throughout expected life of equipment. |
| R-717/R-744 cascade system | Medium | Medium | High | Nil |
|  | Requires new ship with separate machine room or rebuilding | Potential improvement in efficiency. High maintenance cost due to complexity. Require competence, but inexpensive refrigerant | Highly complex relative to on-board capabilities. Additional safety risk of ammonia (lower flammable and toxic), Training required in new markets | No environmental policy risk throughout expected life of equipment. |
| R-744 system | Medium | Medium | Medium | Nil |
|  | Suitable for existing vessels with replacement of system | Potential improvement in efficiency at the expenses of complexity. Require competence, but inexpensive refrigerant | Some complexity relative to on-board capabilities. Training required in new markets | No environmental policy risk throughout expected life of equipment. |

4.2.2 Option 2 – Refrigerant replacement with plant adjustments

The conversion of an existing plant to a halocarbon refrigerant is a technically and economically feasible option, provided a low-GWP fluid is available for the task. Even if many HFC blends are presently under scrutiny, there is no solution ready at the moment and it is not possible, at this stage, to name a refrigerant that will be the definitive low-GWP substitute to HCFC-22. As is well known, the situation is evolving rapidly and it may be reasonable, nevertheless, to expect in the medium term that a solution will emerge for this type of conversion. The economics of the operation will, of course, depend on the cost of the new refrigerant. Most likely, the possible alternatives will be flammable in category A2 or A2L, thus requiring adequate safety considerations and precautions.

|  | Financial considerations |  | Technology risk (Complexity and performance) | Regulatory and environmental risk (10 years horizon) |
| --- | --- | --- | --- | --- |
|  | Capital investment | Operating expenses |  |  |
|  | Medium | Unknown | Unknown | Unknown |
| Option 2 – Refrigerant replacement with plant adjustments |  |  |  |  |
| Conventional refrigeration plant system operating with low-GWP HFC blend | Suitable for existing vessels with change of components and adjustments | Cost of refrigerants at present unknown flammability must be addressed | No significant change in type of technology and components | Environmental policy risk throughout expected life of equipment unknown at present |

4.2.3 Option 3 – Refrigerant drop-in

For systems with less than 10 to 15 years’ service life, a retrofit using a drop-in refrigerant becomes a feasible option, provided there is such a drop-in. At present, however, there is no low-GWP HFC available on the market that can be used as drop-in for on-board systems. As mentioned above, the situation with alternatives is evolving rapidly so that alternatives for this option may become more apparent in the near future.

|  | Financial considerations |  | Technology risk (Complexity and performance) | Regulatory and environmental risk (10 years horizon) |
| --- | --- | --- | --- | --- |
|  | Capital investment | Operating expenses |  |  |
|  | Unknown | Unknown | Unknown | Unknown |
| Option 3 – Refrigerant drop-in |  |  |  |  |
| Conventional refrigeration plant system operating with low-GWP HFC blend | Requires improvement of refrigerant containment | Cost of refrigerants at present unknown flammability must be addressed | No significant change in type of technology and components | Environmental policy risk throughout expected life of equipment unknown at present |

4.2.4 Option 4 – Maintaining HCFC-22

Considering the current problems in finding proper solutions for the retrofit of on-board systems equipped with HCFC-22, one reasonable option could be to keep using HCFC-22 in the system for a few more years, until the end of the ship life cycle or until a cost and environmentally effective solution becomes available. The time horizon for this type of option should be no more than 4-5 years and the target should be those on-board plants with more than 10-15 years’ service life remaining. Maintaining HCFC-22 would require the contextual execution of some actions that increase operational efficiency.

One aspect to be considered is how to meet regulatory requirement of product importers, especially when non-flagged vessels are involved.

|  | Financial considerations |  | Technology risk (Complexity and performance) | Regulatory and environmental risk (10 years horizon) |
| --- | --- | --- | --- | --- |
|  | Capital investment | Operating expenses |  |  |
|  | Low | High | Low | Very high |
| Option 4 – Maintaining HCFC-22 |  |  |  |  |
| Existing plant, operating with HCFC-22, with improved containment Short term solution (max 4-5 years) May not be practical for all vessels | Requires improvement of refrigerant containment | HCFC-22 price expected to increase | No change in technology Limited supply of HCFC-22 in emergency | HFC-22 phase-out in advanced stages |

4.2.5 Additional considerations

Some additional considerations with regard to replacement and retrofit of refrigerant systems in fishing vessels include the following:

- The only sector where both replacement and retrofit are currently missing a real and final solution is the ultra-low temperature refrigeration, needed for the conservation of sashimi and sushi grade tuna.

- The only sector where both replacement and retrofit are currently missing a real and final solution is the ultra-low temperature refrigeration (lower than -50°C evaporation), that may be needed in some systems for the conservation of sashimi and sushi grade tuna.

- High Ambient Temperature issues do not pose a problem for this specific sector as refrigeration systems are generally cooled by sea water.

- Not-In-Kind technologies (defined as those refrigeration techniques which do not use vapour compression reverse cycle), even though presenting some interesting options for application within the fishing industry, are not expected to be commercially available for the sector in the short term.

# 5	Suitability of alternatives under High Ambient Temperature (HAT) conditions

Based on comments from Parties on TEAP’s first report to OEWG-37, this revised chapter provides a more balanced discussion (both positive and negative) of the results as well as additional information on the three testing programs for refrigerants under HAT conditions and includes the following changes and additions:

- Further discussion on the discussion of the methods for considering the impact of the high ambient temperatures on the design of R/AC equipment (see section 5.1); and

- Further information on the reports published for the three projects, which tested alternative refrigerants at temperatures above 35°C and including tabulated summaries of each of the three projects (see section 5.2).

## 5.1 		Influence of HAT conditions on R/AC equipment design

As mentioned previously in the TF reports, HAT conditions are an important issue for the design of R/AC systems. Ambient temperatures are also used in cooling load calculation and building envelope design.

As the ambient temperature increases, system load increases and capacity decreases. With increasing ambient temperatures, the condensing pressure and compressor discharge temperatures also increase, thus leading to possible reliability issues. ISO and EN (European Standards) prescribe pressures corresponding to certain design temperatures for the safe operation of a system. This information is required by design engineers to specify material and pipe wall thickness requirements in a system. Table 5-1 is taken from EN378-2:2008 and the equivalent ISO 5149 based on IEC 60721-2-1.

Table 5-1: Specified Design Temperatures

| Ambient Conditions | < 32°C | < 38°C | < 43°C | < 55°C |
| --- | --- | --- | --- | --- |
| High pressure side with air cooled condenser | 55°C | 59°C | 63°C | 67°C |
| Low pressure side with heat exchanger exposed to ambient temperature | 32°C | 38°C | 43°C | 55°C |

While normally systems are designed for 35°C (T1 in ISO 5151:2010) with appropriate performance (cf. for example, under standards requirements) up to 43°C in some Parties, the high ambient temperature condition requires a design at 46°C (T3 in ISO 5151:2010) with appropriate operation up to 52°C.

High humidity is an important issue even with lower than 35°C temperature conditions for certain Parties. This is because Parties that have high humidity, need high cooling load and thus bigger A/C units when considering the fresh air loads requirement during the selection of the air conditioning units, especially with humidity levels above 60%.

Earlier Task Force reports ((UNEP, 2015) and the March version of the XXVII/4 TF report) already presented methods to assess temperature conditions using incidence of number of hours, weather profiles, cooling degree days, or bin weather data. These methods can again be summarized as follows.

“Incidence of Ambient Temperatures” is a design method that is based on 0.4%, 1%, 2% and 5% of the time per year --for the last 10 years-- (corresponding to 35, 88, 175 and 438 hours per year) that the temperature exceeds 35, 40 or 45⁰C. It is currently the most used method for determining design conditions for air conditioning and refrigeration, where design tables exist for most cities around the world. Most experts and consultants use this method when they have to make estimates for the cooling capacity of A/C and R equipment. A few use the 0.4 % number, others use 1% or 2 %, but the 5% number (438 hours a year above 35⁰C) is the most often used.

The “Climate Zones” method, is where a map of the world in the ASHRAE Standard 169-2013 defines the various climate zones. Zones defined vary from zone A0 (extremely hot humid) down to climate zone 2B (hot dry). The definition of a climate zone is based on the criteria of Cooling Degree Days (CDD). This indicator uses daily temperature data from weather stations over a period of 15 to 30 years to give a typical average year. The most recent data is Typical Meteorological Year (TMY) defined as TMY 3 for the period 1991-2010, and compares the daily average outdoor temperature with a defined baseline temperature for indoor comfort, in this case 18.3°C (65 F). For example, if the average temperature on a particular day is 26°C (78 F), then that day counts as 13 cooling degree days, as a building’s interior would need to be cooled by 7.2°C (13 F) to reach 18.3°C (65 F).

This method takes in consideration the wet bulb temperature (humidity) in each country;

It has an added advantage in that it differentiates between the Dry and Humid conditions in countries.

The “Bin Weather” Method is based on the system operating pressure. EN378-2:2008 (European Standards) and ISO 5149 (based on IEC 60721-2) prescribe pressures corresponding to certain design temperatures for the safe operation of a system. This information is required by design engineers to specify material and pipe wall thickness requirements in a system. EN378 specifies design conditions at 32, 38, 43, and 55°C but does not specify what is a high ambient temperature. This method is a bit complicated and needs specifying a lot of factors (pressure, density…etc.) which necessitates a lot of data analysis to derive the required final data. It is based on the system pressure values, which can be calculated from the actual design temperature.

Using data from a data base giving temperature measurements in many Parties in the world, some Parties have developed a method for selecting Parties with a high ambient temperature according to their average peak ambient temperature per month during a year. Information on this approach for defining HAT Parties was shared with the Task Force, but as this approach was still under discussion by Parties at OEWG-37, the Task Force only notes this information is available without any further review or evaluation.

## 5.2		Results from research projects

Most of the research and development has traditionally been made at the “standard ambient” of 35°C dry bulb temperature; even lower temperatures are used for some tests (e.g., under Air-Conditioning, Heating, and Refrigeration Institute (AHRI) Standard 210/240). The performance of units at different ambient temperatures would then be simulated or extrapolated. The status of the three research projects testing refrigerant alternatives used in specific equipment operating under high ambient temperature conditions were all made public during the period late 2015/early 2016 giving detailed technical results. The three projects are:

- “Promoting low GWP Refrigerants for Air-Conditioning Sectors in High-Ambient Temperature Countries” (PRAHA) and “Egyptian Project for Refrigerant Alternatives” (EGYPRA);

- the Oak Ridge National Laboratory (ORNL) “High-Ambient-Temperature Evaluation Program for Low-Global Warming Potential (Low-GWP) Refrigerants”, Phase I (and ongoing Phase II); and

- The AHRI Low GWP Alternative Refrigerants Evaluation Program (AREP) Phase I (and ongoing Phase II).

### 5.2.1	PRAHA project

“Promoting low GWP Refrigerants for Air-Conditioning Sectors in High-Ambient Temperature Countries” (PRAHA). PRAHA, which was launched by UNEP/UNIDO is 2013 and completed in 2015, involved custom made prototypes built by manufacturers based in the Gulf Coordination Council countries and tested at an independent lab. The project is implemented at the regional level in consultation with National Ozone Units of Bahrain, Iraq, Kuwait, Qatar, Oman, Saudi Arabia, and the UAE to ensure incorporating the project outputs within the HCFC Phase-out Management Plans (HPMPs) particularly for the preparation of post 2015 policies and action-plans. The project tested 14 prototypes using 5 refrigerants and 9 base units running with HCFC-22 or R-410A.

Building up on PRAHA and the linkage to country phase-out plans, Egypt adopted a similar initiative as part of the HPMP to test refrigerant alternatives for air-conditioning units built in Egypt. The initiative EGYPRA tests more blends in different applications. The initiative was launched back in June 2014 and is expected to have the results by the end of 2016.

Both projects built custom made units and testing was done at independent labs at 35, 46, and 50°C ambient temperatures for PRAHA and an additional 27°C for EGYPRA, with an “endurance” test at 55°C ambient to ensure continuous operation for two hours when units are run at that temperature. The proposed refrigerants are shown in table 5-2 below:

Table 5-2: Alternative refrigerants used in PRAHA and EGYPRA projects

| Comparable to HCFC-22 | Comparable to R-410A |
| --- | --- |
| R-290 | HFC-32 |
| R-444B (L-20) | R-447A (L-41-1) |
| DR-3 | R-454B (DR-5A) |
| R-457A (ARM-20a) | ARM-71a |

Table 5-3 shows the result from the testing of the prototypes and their comparison to their respective base units. The table shows the type of equipment tested, the laboratory at which it was tested, the baseline refrigerant against which the porotype is compared, and the constraints and the modifications that were included with the prototype. The table then compares each type of alternative refrigerant to the base unit for COP (efficiency) and capacity at 35°C and a higher ambient temperature which in this case is 50°C.

Table 5-3 PRAHA results for cooling capacity and efficiency as percentage compared to  the baseline units

| Equipment type | Lab utilized | Baseline refrigerant | Prototype Criterion | Refriger-ant tested | COP % comp to baseline @ 35°C | Capacity % comp to baseline @ 35°C | COP % comp to baseline @ 50°C | Capacity % comp to baseline @ 50°C |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 18,000 Btu/hr. Window Unit | Intertek - USA | HCFC-22 COP = 3.14 at 35°C and 2.26 at 50°C for OEM A COP = 2.76 at 35°C and 2.02 at 50°C for OEM B | Custom built prototypes to fit in the same box dimension as the base unit. Expansion device and charge amount designed to meet a minimum specified EER | L-20 (OEM A) | -11% | 9% | -10% | 7% |  |
|  |  |  |  | L-20 (OEM B) | -2% | -6% | -5% | -10% |  |
|  |  |  |  | DR-3 (OEM A) | -9% | 2% | -2% | 1% |  |
| 20,000 Btu/hr. split system | Intertek- USA | HCFC-22 COP = 2.75 at 35°C and 1.94 at 50°C for OEM C COP = 2.52 at 35°C for OEM D | Custom built prototypes to fit in the same box dimension as the base unit. Expansion device and charge amount designed to meet a minimum specified EER | HC-290 (OEM C) | 4% | 8% | -2% | 5% |  |
|  |  |  |  | L-20 (OEM D) | -19% | 7% | -76% | -78% |  |
|  |  |  |  | DR-3 (OEM D) | -27% | -33% | -28% | -31% |  |
| 24,000 Btu/hr. split system | Intertek- USA | R-410A COP = 3.52 at 35°C and 2.30 at 50°C for OEM E COP = 3.08 at 35°C and 2.02 at 50°C for OEM F | Custom built prototypes to fit in the same box dimension as the base unit. Expansion device and charge amount designed to meet a minimum specified EER | HFC-32 (OEM E) | -1% | 15% | -2% | 16% |  |
|  |  |  |  | HFC-32 (OEM F) | -9% | 8% | -22% | -1% |  |
|  |  |  |  | L-41 (OEM E) | -10% | 20% | -7% | 22% |  |
| 36,000 Btu/hr. Ducted Split | Intertek - USA | HCFC-22 COP = 2.83 at 35°C and 1.91 at 50°C for OEM G | Custom built prototypes to fit in the same box dimension as the base unit. Expansion device and charge amount designed to meet a minimum specified EER | L-20 (OEM G) | 0% | -7% | 2% | -5% |  |
|  |  |  |  | DR-3 (OEM G) | -18% | -25% | -13% | -21% |  |
| 36,000 Btu/hr. Ducted Split | Intertek - USA | R-410A COP = 2.79 at 35°C and 1.84 at 50°C for OEM G | Custom built prototypes to fit in the same box dimension as the base unit. Expansion device and charge amount designed to meet a minimum specified EER | HFC-32 (OEM G) | -1% | -4% | -12% | -18% |  |
| 90,000 Btu/hr. Rooftop by Intertek | Intertek-USA | HCFC-22 COP = 2.95 at 35°C and 2.07 at 50°C for OEM H | Custom built prototypes to fit in the same box dimension as the base unit. Expansion device and charge amount designed to meet a minimum specified EER | L-20 (OEM H) | 1% | 6% | -3% | 5% |  |
|  |  |  |  | DR-3 (OEM H) | -3% | -1% | -6% | -4% |  |
|  | Notes on the terms in the table: |  |  |  |  |  |  |  |
| 1 | Efficiency (COP) is measured in Watts of cooling per Watt of input; |  |  |  |  |  |  |  |
| 2 | PRAHA did measurements at 35, 46 and 50°C ambient temperatures; |  |  |  |  |  |  |  |
| 3 | For a full description of refrigerant alternatives and their GWP values, please refer to the relevant chapter on refrigerants in this report; |  |  |  |  |  |  |  |
| 4 | Test conditions are as follows: For 35°C ambient, indoor 26.67°C and 50% relative humidity (AHRI –A. For 50°C ambient, indoor 29°C and 50% relative humidity |  |  |  |  |  |  |  |
| 5 | Cells shaded grey show results that are not consistent with other results for the same refrigerant and could be the results of optimization or design issues. |  |  |  |  |  |  |  |

The outcomes of the PRAHA project, other than the testing results, are:

- There is a need to do risk assessment studies at HAT conditions in Parties that experience HAT conditions;

- There is a need for a full product re-design taking into consideration the technical issues of heat exchanger optimisation, expansion device selection, charge optimisation, excessive pressure, temperature glide, flammability, oil, and energy efficiency issues;

- The economic impact is still to be considered when the availability and cost of components have been determined by market factors. Todays’ price on the market of components is not representative for the cost in the longer term, so alternative methods have to be used to analyse future cost;

- There is need for field testing of the units once a design and alternative refrigerants have been selected by the concerned original equipment manufacturers (OEMs).

For EGYPRA, all prototypes are ready and have been tested at the respective manufacturers. The process of testing the prototypes and base units at the independent lab will start soon and results are expected at the end of the year.

The work by PRAHA and EGYPRA will facilitate the technology transfer and the exchange of experience with low-GWP alternatives for air-conditioning applications operating in high-ambient temperature Parties. The other indirect objective is to encourage the development of local/regional codes and standards that ease the introduction of alternatives needing special safety or handling considerations, and to ensure that national and regional energy efficiency programs are linked to the adoption of low-GWP long term alternatives (PRAHA, 2013).

### 5.2.2	ORNL Project

“High-Ambient-Temperature Evaluation Program for Low-Global Warming Potential (Low-GWP) Refrigerants” by the Oak Ridge National Laboratory (ORNL). ORNL conducted tests using two “soft-optimized” ductless mini-split air conditioners having a cooling capacity of 5.25 kWh (1.5 TR). One unit which was designed to operate with HCFC-22 refrigerant was used for alternative refrigerants that are equivalent in characteristics to HCFC-22, while the other which was designed to use R-410A refrigerant tested the R-410A alternatives. Eighty-four tests were conducted in total for a total of 10 alternative refrigerants at ambient temperatures varying from 27 to 55°C.

Table 5-4: Alternative refrigerants used in ORNL Project

| Comparable to HCFC-22 | Comparable to R-410A |
| --- | --- |
| N-20b | HFC-32 |
| DR-3 | R-447A (L-41-1) |
| ARM-20b | DR-55 |
| R-444B (L-20a) | ARM-71a |
| R-290 | HPR-2A |

Table 5-5 shows the results for the ORNL project taken from the various reports available online. ORNL tested two base units and then changed the refrigerant as well as certain components and settings to test the alternative refrigerants.

Table 5-5 ORNL results for capacity and efficiency as percentage compared to the baseline units

| Equipment Type |  |  | Lab utilized |  | Baseline Refrigerant | Equipment Criterion | Refriger. Tested | COP % comp to baseline @ 35°C | Capacity % comp to baseline @ 35°C | COP % comp to baseline @ 52°C | Capacity % comp to baseline @ 52°C |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 18,000 Btu/hr. Split unit (Carrier) |  |  | ORNL |  | HCFC-22 COP = 3.07 at 35°C and 1.98 at 52°C | Same machine to test all refrigerants. Criteria: matching superheat and sub cooling to base unit. Changing expansion devise. Charge level optimized at 35C | N-20B | -13% | -14% | -11% | -15% |  |
|  |  |  |  |  |  |  | DR-3 | -16% | -12% | -14% | -12% |  |
|  |  |  |  |  |  |  | ARM-20B | -12% | -3% | -11% | -3% |  |
|  |  |  |  |  |  |  | R-444B (L-20A) | -11% | -9% | -7% | -4% |  |
|  |  |  |  |  |  |  | HC-290 | 7% | -8% | 7% | -4% |  |
| 18,000 Btu/hr. split unit (Carrier) |  |  | ORNL |  | R-410A COP = 3.4 at 35°C and 2.07 at 52°C | Same machine to test all refrigerants. Criteria: matching superheat and sub cooling to base unit. Changing expansion devise. Charge level optimized at 35C | HFC-32 | 4% | 5% | 5% | 11% |  |
|  |  |  |  |  |  |  | DR-55 | 3% | -3% | 3% | 0% |  |
|  |  |  |  |  |  |  | R-447A (L-41) | -5% | -14% | 3% | -6% |  |
|  |  |  |  |  |  |  | ARM-71a | -1% | -8% | 2% | -4% |  |
|  |  |  |  |  |  |  | HPR-2A | -2% | -9% | 5% | -1% |  |
|  |  |  | Notes on the terms in the table |  |  |  |  |  |  |  |  |
| 1 | Efficiency (COP) is measured in Watts of cooling per Watt of input; |  |  |  |  |  |  |  |  |  |
| 2 | ORNL did measurements at 27.8, 35, 52 and 55°C ambient temperatures; |  |  |  |  |  |  |  |  |  |
| 3 | For a full description of refrigerant alternatives and their GWP values, please refer to the relevant chapter on refrigerants in this report; |  |  |  |  |  |  |  |  |  |
| 4 | Test conditions are as follows: For 35°C ambient, indoor 26.7/19.4°C (AHRI-A). For 52°C ambient, indoor = 29/19°C. |  |  |  |  |  |  |  |  |  |

The ORNL/TM-1015/536 report has the following conclusion appearing as part of its Executive Summary (reproduced here without changes):

“The test results from this evaluation program demonstrate that there are several viable alternatives to both R-22 and R-410A at high ambient temperatures. In some cases, there was a significant improvement in the performance of the alternatives over that of the baseline, in terms of both COP and cooling capacity. In other cases, the performance of the alternatives fell within 10% of the baseline, which suggests that parity with baseline performance would likely be possible through additional engineering design.

The R-22 alternative refrigerants showed promising results at high ambient temperatures: although both of the A1 alternative refrigerants lagged in performance, some of the A2L refrigerants showed capacity within 5% and efficiency within approximately 10% of the baseline system. The A3 refrigerant (R-290) exhibited higher efficiency consistently; however, it did not match the cooling capacity of the baseline system. The most promising A2L refrigerants exhibited slightly higher compressor discharge temperatures, while the A3 refrigerant exhibited lower compressor discharge temperatures.

The R-410A alternative refrigerants are all in the A2L safety category. Most of them showed significant potential as replacements. R-32 was the only refrigerant that showed consistently better capacity and efficiency; however, it resulted in compressor discharge temperatures that were 12–21°C higher than those observed for the baseline refrigerant. These higher temperatures may negatively impact compressor reliability. DR-55 and HPR-2A had higher COPs than the baseline and matched the capacity of the baseline at both the hot and extreme test conditions. R-447A and ARM-71a had lower cooling capacity than the baseline at all ambient conditions. The system efficiency of R-447A showed improvement over the baseline at high ambient temperatures; for ARM-71a, the efficiency was similar to the baseline at all test conditions.

The efficiency and capacity of the alternative refrigerants could be expected to improve through design modifications that manufacturers would conduct before introducing a new product to market. However, given that the scope of this study covered only soft-optimized testing, no detailed assessment can be made of the extent of potential improvements through design changes. Within the bounds of what is possible in optimizing the units for soft-optimized tests, the ORNL test plan included only minor optimizations, including refrigerant charge, capillary tube length, and lubricant change. Therefore, these are conservative results that probably could be improved through further optimization. Additional optimization, including heat transfer circuiting and proper compressor sizing and selection, would likely yield better performance results for all of the alternative refrigerants.

Losses in cooling capacity are typically easier to recover through engineering optimization than are losses in COP. The primary practical limit to improvements in capacity is the physical size of the unit; but that is not expected to be a significant concern in this case, based on the magnitude of the capacity losses exhibited in this evaluation program. Thus, the COP losses and the increases in compressor discharge temperature are particularly important results of this testing program, in that these variables will be the primary focus of future optimization efforts.

This performance evaluation shows that viable replacements exist for both R-22 and R-410A at high ambient temperatures. Multiple alternatives for R-22 performed well. Many R-410A alternatives matched or exceeded the performance of R-410A. These low-GWP alternative refrigerants may be considered as prime candidate refrigerants for high ambient temperature applications. Before commercialization, engineering optimization carried out by manufacturers can address performance loss, the increase in compressor discharge temperature that many alternatives exhibited (particularly the R-410A alternatives), and any safety concerns associated with flammable alternatives.” (Abdelaziz, 2015)

Phase II: ORNL started the second phase of the program testing “Low GWP Refrigerants in High Ambient Temperature Countries” in February 2016, covering roof-top air conditioners in this phase. Results will be published in the second half of 2016.

### 5.2.3	AREP Project

“Low GWP Alternative Refrigerants Evaluation Program” (AREP) Phase-II. The project was launched by the Air-Conditioning, Heating, and Refrigeration Institute (AHRI) is a cooperative research program to identify suitable alternatives to high GWP refrigerants without prioritizing them. In the first phase of the project, 21 international companies evaluated 38 refrigerant candidates for replacing HCFC-22 and three HFCs, R-410A, HFC-134a, and R-404A (Amrane, 2013), in applications varying from air conditioners and heat pumps (both package, split and variable refrigerant flow), chillers (screw and centrifugal), refrigeration (commercial and ice machines), refrigerated transport, and bus air-conditioning. Phase II tested 17 refrigerants plus doing more tests at high ambient temperature conditions.

Table 5-6: AREP Phase II low-GWP High Ambient testing

| AREP Phase II Low-GWP High Ambient Test Matrix |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Product | Test companies | High Ambient Conditions | Baseline Refrigerant | ARM-71a | DR-5A | DR-55 | HPR2A | L-41-1 | L-41-2 | HFC-32 |
| 34 MBH chiller | Armines | 115F | R-410A |  | X |  |  | X | X | X |
| 14 SEER 3-ton HP | Carrier | 125F | R-410A | X | X |  | X | X | X |  |
| 13 SEER 3-ton HP | Danfoss | 115F and 125F | R-410A |  | X |  |  |  | X* | X** |
| 14 SEER 3-ton split HP | Goodman | 115F and 125F | R-410A |  |  |  |  |  |  | X*** |
| 5-ton packaged | Lennox | 115F | R-410A | X | X | X | X |  | X | X |
| 4-ton packaged | Trane | 125F | R-410A |  | X | X |  |  |  | X |
| 6-ton packaged | Zamilac | 125F | R-410A |  |  |  |  |  |  | X |

* L-41-2 at wet suction, no HAT

**HFC-32 with same charge and with optimized charge

*** HFC-32 with standard POE oil and with prototype POE oil

For high ambient testing, seven entities tested three residential split units, four rooftops, one chiller, and several compressors. The results were compared to baseline of R-410A units. Refrigerant candidates are shown in table 5-8 below (Schultz, 2016a). Refrigerants were tested at 115 F (46.1°C) and 125 F (52.6°C). The tests were either a drop-in or a soft optimization with a change in refrigerant charge and/or expansion device.

AREP-II was conducted by several entities with different test protocols which contributed to differences in results. The different tests varied from drop-in to soft-optimized tests adjusting the expansion device for similar superheat, or adjusting the charge for a similar sub-cooling. The results shown below are extracted from the test reports of AREP-II that are available publically on-line.

Table 5-7 AREP-II results for capacity and efficiency as percentage compared to the baseline units

| Equip- ment Type | Company | Baseline Refrigerant | Prototype Criterion | Refrigerant Tested | COP % comp to baseline @ 35°C | Capacity % comp to baseline @ 35°C | COP % comp to baseline@ 51.6°C | Capacity % comp to baseline @ 51.6°C |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 36,000 Btu/hr. Split heat pump | Carrier Indiana- polis | R-410A COP = 3.55 at 35°C and 1.87 at 51.6°C | Criteria: Matching superheat and sub cooling to base unit. Charge level determined by criteria and held constant for all temperatures tested | ARM-71A | -1% | -8% | 7% | -3% |
|  |  |  |  | R-454A (DR-5A) | -1% | -6% | 6% | -1% |
|  |  |  |  | HPR2A | -4% | -11% | 3% | -4% |
|  |  |  |  | R-446A (L-41-1) | -2% | -10% | -1% | -3% |
|  |  |  |  | R-447A (L-41-2) | -1% | -7% | -1% | -4% |
| 48,500 Btu/hr. Rooftop | Ingersoll Rand Clarks-ville | R-410A COP = 3.31 at 35°C, 2.00 at 48.9°C and 1.80 at 51.6°C | Adjustable expansion device, Variable Frequency drive matching the capacity with base unit. Varying indoor conditions | DR-55 | 4% | 0% | 3% | 0% |
|  |  |  |  | HFC-32 | 6% | 1% | NA | NA |
|  |  |  |  | DR-5A | 5% | 1% | 7% | 3% |
| 72,000 Btu/hr. Rooftop | Zamil KSA | R-410A COP = 3.57 at 35°C and 2.06 at 51.6°C | Criteria maintained same superheat and sub cooling as base unit by changing expansion devise and adjusting charge. Oil is also different | HFC-32 | 2% | 9% | 10% | 16% |
| 34,000 Btu/hr. split | Goodman USA | R-410A COP = 3.53 at 35°C and 1.82 at 51.6°C | Tested HFC-32 unit with POE oil and withy prototype oil for the same expansion devise and charge determined by superheat | HFC-32 with prototype oil | 3% | 7% | 13% | 14% |
| 60,000 Btu/hr. Rooftop | Lennox USA | R-410A COP = 3.87 at 35°C and 2.07 at 51.6°C | Matching superheat and sub cooling | L-41-2 | 3% | -7% | 10% | -1% |
|  |  |  |  | ARM-71A | 3% | -4% | 10% | 2% |
|  |  |  |  | HPR2A | 1% | -5% | 8% | 1% |
|  |  |  |  | DR-5A | 1% | -4% | 2% | -3% |
|  |  |  |  | HFC-32 | -10% | -4% | -9% | -1% |

|  |  | Notes on terms in the table: |  |
| --- | --- | --- | --- |
| 1 | Efficiency (COP) is measured in Watts of cooling per Watt of input |  |
| 2 | PRAHA did measurements at 35, 46 and 50°C ambient temperatures |  |
| 3 | For a full description of refrigerant alternatives and their GWP values, please refer to the relevant chapter on refrigerants in this report |  |
| 4 | Test conditions are as follows: For 35°C ambient, indoor 26.67°C and 50% relative humidity (AHRI -A). For 50°C ambient, indoor 29°C and 50% relative humidity |  |
| 5 | Cells shaded grey show results that are not consistent with other results for the same refrigerant and could be the results of optimization or design issues |  |

The conclusion from AREP-II (Schultz, 2016a) is that general trends in HAT performance are similar for all alternative refrigerants. Systems with alternatives generally provided similar to higher capacities than R-410A systems at HAT conditions, i.e., showing a smaller decrease in capacity as ambient temperatures increase

### 5.2.4	General remarks on the three research projects

The March TF XXVII/4 report noted that tests under HAT conditions described above illustrate the difficulties of assessing the energy efficiency associated with a refrigerant, considering:

•	Testing temperatures differs from test program to test program;

•	Obviously no single temperature can accurately match a real geographical location, so the results do not relate directly to the actual energy consumption in a real situation;

•	The units used for testing vary within the same test programs;

•	In some tests only the refrigerant is changed, in others the oil is changed or even the compressor;

•	Differences in test protocols further contributed to differences in results, for example: adjusting the expansion device for similar evaporator superheat, adjusting the charge for a similar sub-cooling, or adjusting compressor displacement to match compressor capacity to heat exchanger capacity.

In evaluating the three projects, the following conclusions and comments can be drawn from the technical data presented in the capacity and efficiency tables:

- The measured efficiency of the alternative refrigerants is in the vicinity of plus or minus 15% of the base units to which they were compared;

- The R-410A alternatives give results that are close to the performance of R-410A at HAT. However, the performance of R-410A at HAT is lower than HCFC-22 due to the characteristic of the refrigerant;

- The performance of the prototypes can be further improved through optimization of components and design parameters;

- The safety aspect is important for the high ambient temperature countries as the refrigerant charge is higher than for units operating in lower ambient temperatures.

- The efficiency and capacity of the alternative prototypes are two aspects of the comparison. A more complete comparison would also include a cost comparison; however, there is not enough data on cost, neither for some of the alternative refrigerants nor of the components to have a measurable comparison;

- While efficiency is important to meet the regulatory minimum energy performance standards (MEPS), the capacity of air conditioners at HAT conditions is of utmost importance in order to provide the required indoor comfort when these conditions happen.

- As a general rule, the cost of the equipment depends on the characteristics of the refrigerant and the performance of the equipment at high ambient temperatures. For example, if the capacity of the equipment at HAT is 10% lower for the required efficiency, then a larger machine is needed to meet the required load making the equipment more expensive;

- ORNL and PRAHA came to slightly different conclusion about the performance of alternative refrigerants vs. HCFC-22 with PRAHA generally showing better results. This is due to the fact that the PRAHA prototypes were custom built, while ORNL uses the base unit with some optimisation. From this it can be concluded that results can be improved with customisation. The engineering level of the unit is more important than the refrigerant characteristic.

## 5.3 	Further considerations

Chapter 7 of the September 2015 XXVI/9 Task Force Report (UNEP, 2015) discussed additional topics related to HAT conditions: a definition of options for HAT conditions, design considerations, research projects, energy efficiency and regulations related to energy efficiency, current/future alternative chemicals and technologies for air conditioning under HAT conditions, and considerations for refrigeration systems under HAT conditions including not-in-kind technologies (UNEP, 2015). That information is not repeated here, but in view of the initial results of the testing under HAT conditions discussed above, some of those considerations are further highlighted below.

On energy efficiency: In regions with HAT conditions, legislations which set minimum energy performance standard (MEPS) values on air conditioners are emerging quickly. Most of the Parties require third party verification of declared performance. Higher minimum energy efficiencies are being announced on a regular basis, and this tendency may continue. As examples, Bahrain recently announced MEPS values and regulation of labelling air conditioners and Saudi Arabia is moving closer to releasing their regulation for large air conditioners and chillers expected in the second quarter of 2016.

When selecting new refrigerants, it is important to consider further increases on the current minimum energy efficiency requirements. To the extent increases in MEPS are not met by current models, this offers the opportunity for manufacturers to implement new refrigerants while redesigning equipment for those new refrigerants.

On design and availability: The design for HAT conditions needs special care to avoid excessive condensing temperatures and getting close to the critical temperature for each type of refrigerant. Other issues such as safety, refrigerant charge quantity, and improving the energy efficiency for both partial and full load have to be taken into consideration

In HAT conditions, the cooling load of a conditioned space can be up to three times that for moderate climates. Therefore, larger capacity refrigeration systems may be needed which implies a larger refrigerant charge. Due to the requirements for charge limitation according to certain safety standards, the possible product portfolio suitable for high ambient conditions is more limited than for average climate conditions when using the same safety standards.

As concluded from the testing projects, special design of both components and products is needed for the new alternatives to meet the performance of systems in both capacity as well as efficiency requirements. While the commercialization process of refrigerants can take up to ten years, as seen from chapter 2, the commercialization of products using these alternatives will take further time.

As HCFC-22 air conditioning products get phased-out for some applications, the industry is turning to available technology using higher GWP refrigerants with higher discharge pressures such as R-410A or comparable pressures like R-407C, depending on the application. One exception is HFC-32 which has seen a limited release for room air conditioners following the change-over in Japan. HC-290 products, which have potential due to the favourable performance of HC-290 compared to HCFC-22 at HAT conditions, are not yet commercially available in many Parties although some of the local suppliers are busy researching and designing such products.

On retrofits: It is important to note that any change of refrigerant in an existing design requires careful considerations. Theoretical calculations can give an idea about what is generally to be expected with a change in refrigerant, but specific details on the system design are needed. Modifying the electrical connections to meet the requirements needed for flammable refrigerants is an additional cost that needs to be taken into consideration. This cost is the same for class A3 or class A2L refrigerants and mostly due to changing the location of the controls in order to reduce the risk of a spark.

For HAT conditions, the design and sizing of the heat exchanger will impact how the system capacity and energy efficiency is influenced by a change in refrigerant. For system builders this means that each system design needs to be optimized for each type of refrigerant. This requires an investment similar to what has been spent on optimizing the system for the current refrigerant, and for highly cost optimized systems this investment might be considerable.

On safety: Standards for the new refrigerants (that are mostly flammable), such as ISO 5149, EN 378, IEC 60335-2-40 for air conditioners and heat pump systems and IEC 60335-2-89 for some commercial refrigeration appliances, are available, although IEC 60335-2-89 needs to be adapted to allow larger charges of flammable refrigerants that are required for the bigger capacities of air conditioners working at HAT conditions. IEC standards are a de facto legal requirement in several Parties as the Certification Body (CB) scheme is the actual requirement for import and sales of products. In some Parties, the implementation of old standards in the legislation, for instance building codes or other mandatory safety regulations, blocks the uptake of especially flammable refrigerants.

Another important aspect of safety standards is that their value is tied to the degree of compliance, and this makes training of system builders and service technicians an important part of implementing safety standards. The cost of the above certification, including the third-party certification cost and including the training cost, should be considered.

Although risk assessment work on flammable refrigerants is an on-going research in some Parties, there is a need for a comprehensive risk assessment for class A3 and A2L refrigerant alternatives at installation, servicing and decommissioning practices at HAT conditions and when field testing the units.

## 5.4	References

Abdelaziz, 2015	Abdelaziz, O. et al., 2015. Alternative Refrigerant Evaluation for High-Ambient-Temperature Environments:R-22 and R-410A Alternative for Mini-Split Air Conditioners, ORNL/TM-1015/536

Amrane, 2013	Amrane, K. Overview of AHRI Research on Low-GWP Refrigerants. Webinar, August 2013

ASHRAE, 2013	ASHRAE Handbook – Fundamentals. 2013

Burns, 2016	Burns, L. System Drop-in Tests of R-410A Alternative Refrigerants ARM-71a, R-454B, HPR2A, R-446A, R-447A in a Heat Pump. AHRI conference, Orlando, January 2016.

Chakroun, 2016	Chakroun, W. Evaluating Low-GWP Refrigerants for Air-Conditioning Industry in High Ambient Temperature Countries, Methodology and Final Results. ASHRAE Conference, Orlando, January 2016.

EN378-2:2008	The European Standard for the design and construction of refrigeration systems “Refrigerating systems and heat pumps — Safety and environmental requirements”. 2008.

IEC 60721-2-1	International Electro-technical Commission, “Classification of environmental conditions - Part 2-1: Environmental conditions appearing in nature - Temperature and humidity”. 2013

ISO 5151:2010 	International Organization for Standardization (ISO). Non-ducted air conditioners and heat pumps -- Testing and rating for performance.

Li, 2016	Li, S. Soft-optimization test of R-410A alternative Refrigerant R-32 in a split condensing unit. AHRI conference, Orlando, January 2016

PRAHA, 2013 	PRAHA project document, 2013

Schultz, 2016a	Schultz, K. Summary of High Ambient Temperature (HAT) Tests, Conducted Under AREP II, AHRI Conference, Orlando, January 2016

Schultz, 2016b	Schultz, K. Soft-Optimized System Test of R-410A, DR-55, R-32, and DR-5 in a 4-RT Unitary Rooftop Heat Pump. AHRI conference, Orlando, January 2016

UNEP, 2015	UNEP, Update Decision XXVI/9 Task Force report, Additional information on alternatives to ozone-depleting substances, September 2015, ISBN 978-9966-076-14-4

Zoughaib, 2016	Zoughaib, A. System Drop in Test of R-410A Alternative Refrigerant DR5A, L1-1, L41-2, R32 and ARM71a in a Water Chiller. AHRI conference, Orlando, January 2016.

# 6	BAU and MIT scenarios for Article 5 and non-Article 5 Parties for 1990-2050: Refrigeration and Air Conditioning

This chapter contains the same presentation of scenarios as the March 2016 version of the XXVII/4 Task Force report. Based on comments from Parties on that report at OEWG-37, this revised chapter also contains the following changes and additions:

- Consideration of existing regulations as well pending regulations in non-Article 5 Parties and the impact of the latter (see section 6.1);

- Comparison of the demand in non-Article 5 Parties between a BAU scenario with regulations considered (up to 2050) and without regulations considered (up to 2030) (see section 6.4.1 and Figure 6-3);

- A revised table on growth percentages for the various R/AC subsectors, for both the new manufacturing and the total demand (in the March version of the XVII/4 TF report certain percentages of decreasing HCFC demand had been included in the total percentages by mistake) (see section 6.2 and Table 6-1);

- Additional information on the production of various HFCs, not only the important ones for the R/AC sector (see section 6.3 and Table 6-2);

- Addition of an 18-year manufacturing conversion period for the Article 5 MIT-3 scenario and its impact on total demand (see section 6.5);

- Related to this chapter, Annex 3 to this report provides an overview of final regulations from the EU, USA, and Japan addressing HFCs considered for the scenarios and Annex 4 contains updated tables for total, new manufacturing, and servicing demand; and

- Costs estimates have not changed as presented in previous Task Force reports.

The chapter is organized as follows:

6.1    	Expansion of scenarios

6.2 	Method used for calculation

6.3 	HFC consumption and production data

6.4 	Non-Article 5 scenarios

6.5 	Article 5 scenarios

6.6	Demand and benefit numbers

## 6.1		Expansion of scenarios

The previous Decision XXVI/9 paragraph 1 (c) asks to revise the scenarios: “Taking into account the uptake of various existing technologies, revise the scenarios for current and future demand elaborated in the October 2014 final report on additional information on alternatives to ozone-depleting substances of the Technology and Economic Assessment Panel’s task force on decision XXV/5, and improve information related to costs and benefits with regard to the criteria set out in paragraph 1 (a) of the present decision, including reference to progress identified under stage I and stage II of HCFC Phase-out Management Plans”.

The current Decision XXVII/4 requests to expand the scenarios to the period 1990-2050, twenty years after 2030 which was the last year in the scenarios used in the XXVI/9 Task Force report (UNEP, 2015).

The following scenarios have again been calculated, which apply to the R/AC sector only for this first report of the XXVII/4 Task Force submitted to OEWG-37:

- A BAU scenario: The Task Force is aware of various regulations and actions as well as pending regulations applied by Parties. This implies that the F-gas regulation in the European Union (EU) and regulations in the United States (US), making certain HFCs unacceptable for certain sub-sectors by specific dates, have been considered as their impacts are very specific to the R/AC sectors and sub-sectors (see also Annex 3, where specific elements of these regulations are given; the final regulation of Japan has not been incorporated in the BAU scenarios considered in this study). This implies that, in the business-as usual (BAU) calculation, certain high GWP substances in specific subsectors are replaced by low or lower  GWP substances. In this way it responds to comments the XXVI/9 Task Force already received at OEWG-36 and at MOP-27. The changes incorporated mainly apply to commercial refrigeration and, to a small degree, to stationary air conditioning. In Article 5 Parties, economic growth percentages expected for the period 2015-2050 are virtually the same as the ones in the XXVI/9 report. In this report, the impact of a BAU scenario without and with certain national or regional legislations is shown.

- An MIT-3 scenario: A 2020 completion of conversion in non-Article 5 Parties of all R/AC sub-sectors and the start of the manufacturing conversion of all R/AC sub-sectors in 2020 in Article 5 Parties, now with consequences for the period 2020-2050.

- An MIT-4 scenario: This is the same as the MIT-3 scenario, but with the assumption of 2025 for the start of the manufacturing conversion for stationary AC in Article 5 Parties, now with consequences for the period 2020-2050.

- An MIT-5 scenario: This is the same as the MIT-3 scenario, but with the assumption of a 2025 completion of conversion in non-Article 5 Parties of all R/AC sub-sectors and the start of the manufacturing conversion of all R/AC sub-sectors in 2025 in Article 5 Parties, now with consequences for the period 2020-2050

For Article 5 Parties, manufacturing conversion projects would need preparation to be funded; it would also take a certain period of time before conversion projects would have been approved by a funding authority, so that they can be initiated. Finally, experience with CFCs and HCFCs has shown that, the slower the conversion of manufacturing, the longer the servicing tail will be, i.e., the longer servicing of equipment will be required (see sections 6.5.3 and 6.5.5 taken from (UNEP, 2015)).

In this chapter the 1990-2050 scenarios will be given in the following sequence. First, the BAU scenario for non-Article 5 Parties will be dealt with, which will be analysed in tonnes and ktonnes CO2-eq. This is then followed by the MIT-3 and MIT-5 scenarios for non-Article 5 Parties; new manufacturing and servicing figures are given in ktonnes CO2-eq. (not in tonnes). As a next step, the Article 5 scenarios are given. Again, first the BAU scenario for Article 5 Parties will be dealt with, which will be presented in tonnes and ktonnes CO2-eq. This is then followed by the MIT-3, MIT-4 and MIT-5 scenarios for Article 5 Parties; new manufacturing and servicing figures are given in tonnes and in ktonnes CO2-eq.

## 6.2 		Method used for calculation

A “bottom-up” method has been used to predict the demand for R/AC equipment, as in the XXVI/9 Task Force report (UNEP, 2015). The RTOC 2010 Assessment Report (RTOC, 2010) describes the bottom-up method used here. A bottom up method derives the size of banks from information obtained from outside (accountancy reports on trade and exports, if possible, supplemented with a trend analysis). The banks serve to calculate emissions using agreed emission parameters. As a result, the demand (or “consumption”) can be calculated, which consists of (1) what is supplied to the existing banks (i.e., to compensate for leakage), and (2) what is added to the bank (i.e., in new equipment that has been charged) ), less (3) what is recovered and reused from the bank (i.e., material reclaimed from equipment decommissioned). In a spreadsheet analysis, this can be seen as one stream of refrigerant into a bank with equipment that has been manufactured over a number of years. In summary, the refrigerant demand or the annual sales of new or virgin refrigerant are equal to the amount of refrigerant introduced into the R/AC sector in a country (or regions) in a given year. It includes all the chemicals used for charging or recharging equipment, whether the charging is carried out in the factory, in the field after installation, or whether it concerns recharging with the appropriate equipment during maintenance operations.

In this type of “bottom-up” approach, one therefore evaluates the consumption of a certain refrigerant based on the numbers of equipment in which the fluid is charged, e.g. refrigerators, stationary air-conditioning equipment, and so on. It requires the establishment of an inventory of the numbers of equipment charged with substances (which then forms the total inventory, or the “bank”), and the knowledge related to their average lifetime, their emission rates, recycling, disposal, and other parameters. The annual emissions are estimated as functions of all these parameters during the entire equipment lifetime.

Further information on sub-sectors, equations used and information on how the installed base is being considered can be found in the XXVI/9 TF report (UNEP, 2015). As in this XXVI/9 report, the GWP for low GWP replacement refrigerants has been chosen as follows. In domestic refrigeration the use of isobutane is assumed with a very low GWP. In cases where the replacement refrigerant is known (ammonia, hydrocarbons), very low GWP factors have been used. For commercial refrigeration, one can assume the use of carbon dioxide, pure low-GWP refrigerants or refrigerant blends in supermarkets, low GWP hydrocarbons in mass produced units, blends or carbon dioxide in condensing units (where an average GWP of 300 is used). For stationary AC as a whole, an average GWP of 300 has also been used (as an estimated average between very low GWP refrigerants and others, such as HFC-32 and various blends under investigation). The choice has been made on the basis of an averaging exercise, not related to GWP considerations presented in Table 2-6. In Mobile Air Conditioners (MACs), replacement refrigerants are assumed to have negligible GWP.

Table 6-1: Growth rates for high-GWP HFC demands in the various R/AC sub-sectors (manufacturing and total) during the periods 2010-2020, 2020-2030 and 2030-2050

| Non-Article 5 Parties |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sub-sector |  | 2010-2020 | 2020-2030 | 2030-2050 |
| Domestic refrigeration | Manufact. | -6.0% | -1.5% | 3% |
|  | Total | -6.0% | -1.5% | 3% |
| Commercial refrigeration | Manufact. | -10.5% | 0.1% | 3% |
|  | Total | -2.0% | -5.5% | 2.1% |
| Industrial refrigeration | Manufact. | -2.1% | -1.8% | 3% |
|  | Total | 0% | -1.2% | 1.8% |
| Transport refrigeration | Manufact. | -9.5% | -4% | 3% |
|  | Total | -1.3% | -0.2% | 0.9% |
| Stationary AC | Manufact. | 5.8% | 3% | 3% |
|  | Total | 8.5% | 2.8% | 2.7% |
| Mobile AC | Manufact. | -12.5% | 3.3% | 3% |
|  | Total | -3.6% | -5.5% | 1.9% |
| Article 5 Parties |  |  |  |  |
| Sub-sector |  | 2010-2020 | 2020-2030 | 2030-2050 |
| Domestic refrigeration | Manufact. | 5.8% | 5.8% | 4.5% |
|  | Total | 4.8% | 5.8% | 4.5% |
| Commercial refrigeration | Manufact. | 12.9% | 8.6% | 4.5% |
|  | Total | 16.5% | 9.6% | 5.1% |
| Industrial refrigeration | Manufact. | 8.8% | 6.8% | 3.7% |
|  | Total | 6.1% | 6.1% | 4.2% |
| Transport refrigeration | Manufact. | 5.8% | 4.5% | 4.5% |
|  | Total | 9.5% | 5.7% | 4.4% |
| Stationary AC | Manufact. | 15.8% | 6.0% | 1.5% |
|  | Total | 17.7% | 8.3% | 3.0% |
| Mobile AC | Manufact. | 5.0% | 5.0% | 5.0% |
|  | Total | 6.4% | 5.0% | 5.0% |

Note: this table is different from the one in the March 2016 TF report, since some negative growth in HCFC demand was taken into account in the first 10 (20) years (2010-2030) in Article 5 Parties

Growth rates for equipment production have been slightly changed (in two cases) compared to the rates used in the XXVI/9 Task Force report, in order to give a more realistic approach in the period after 2030. In this report, the growth rates apply as given in Table 6-1 above.

A number of considerations substantially complicate the calculations. This includes the preference to apply certain alternatives in specific equipment (and often under certain conditions), combined with the fact that the R/AC banks -the amounts present in the equipment- need recharging (i.e., servicing) over the entire lifetime of the equipment. Details on lifetime and annual leakage are given in (Table 5-2 in) the XXVI/9 report (UNEP, 2015).

The calculation method covers the period from 1990 until 2050, the latter year as requested in Decision XXVII/4. Table 6-1 gives the growth rates assumed for new manufacturing in the various R/AC sub-sectors, as well as for the total demand (manufacturing and servicing). The growth rate assumed in the manufacturing sector is only one parameter in the scenario calculations. The total demand for a sub-sector is calculated using parameters such as equipment lifetime, equipment leakage, charge at new manufacturing etc. This implies that, if the annual growth rate in a manufacturing sub-sector would be 1-5%, the annual growth rate of the total demand for that subsector can be a few percent higher, e.g., varying from 2 up to 5-6%. These percentages can also be derived from the BAU Tables 6-7 and 6-8 and from the more detailed tables as given in Annex 4.

Depending on the application sector, uncertainties are different either because activity data include different uncertainties or because emission factors may vary significantly from one Party to the other. The 2010 RTOC Assessment Report (RTOC, 2010) describes a simple approach that gives a quality index expressed in percentages. Further elaboration can be found in the XXVI/9 report. Uncertainties in banks are estimated at 12.5-22.5%, uncertainties in emissions 12.8-37%, specific numbers are dependent on the sub-sector. For the total R/AC sector, the uncertainty range in the demand calculated ranges from -10% to +30%.

The bank of refrigerants is substantially larger (10-20 times) than the annual demand. In fact the bank as calculated determines the amount of emissions, dependent on leakage assumptions during operation. The total demand is the sum of the amount used for new manufacturing and for re-charging to balance the refrigerant lost via all emissions types. Banks of refrigerants could be given for regions and/or for certain Parties as used in the model, but the amounts that would then be presented would not contribute to a better understanding of the demand, which is the essential parameter in this chapter that deals with demand scenarios.

As already mentioned in the Decision XXVI/9 TF September Update Report (UNEP, 2015), estimates should be cross-checked with reported HFC consumption and production data, specified per refrigerant. For the most recent cross-check, information can be found below.

## 6.3		HFC production and demand (consumption) data

Estimates for global 2012 and 2015 production of the relevant HFC chemicals can be made by combining UNFCCC data, manufacturer’s estimates for production capacity as well as global emission data. This was already given in the XXVI/9 Task Force report (UNEP, 2015).

Data on HFC emissions are reported annually by developed countries, i.e., the Annex I Parties under the UNFCCC Kyoto Protocol; these emission data are estimated (calculated) by national agencies.

HFC consumption and production data are also reported by developed countries, i.e., the Annex I Parties to the UNFCCC. Even when certain consumption and production data are missing (i.e., data not reported by some countries, or reported as HFCs in general), these reports enable a first estimate for the production of most HFCs in the Annex I Parties to be made.

Estimates for HFC production in the Article 5 Parties are often made by non-Article 5 chemical manufacturers (Kuijpers, 2015). Based on global consumption calculations, estimates for HFC production were also made by McCulloch (2015). Furthermore, global emissions data for several HFCs are available from certain literature sources, e.g. from Montzka (2015). Recently, Chinese HFC (and HCFC) production data up to the year 2013 were reported by Kaixiang (2015).

Further HFC production estimates from Chinese manufacturers were also obtained in the period May-July 2015 (Kuijpers, 2015). The HFCs considered above are HFC-32, HFC-125, HFC-134a and HFC-143a, but also HFC-152a, HFC-227ea, HFC-236fa and HFC-245fa.

However, this report uses almost the same estimates (as in the XXVI/9 report) for HFC production of the four main HFCs (the ones important for R/AC) in Table 6-2 below (the estimated production of HFC-134a in one country has been added that was not included in the XXVI/9 Task Force report). As mentioned, these four HFCs are the main ones used in the R/AC sector, except for HFC-134a, which is also applied in several other sectors (such as foams, aerosols, MDIs).

The table shows a total HFC production of about 510 ktonnes for these four (main) HFCs, which is a forecast for the year 2015 (this can be translated to about 930 Mt CO2-eq., if calculated in climate terms). The global production capacity for these four HFCs is estimated at a much higher level, at about 750 ktonnes (Campbell, 2015).

It needs to be emphasised that the global HFC production (for these four main HFCs) determined in this way is estimated to have a ±10% uncertainty for the separate HFC chemicals, which implies that the 510 ktonnes value roughly has a 5% uncertainty value (495-535 ktonnes).

Estimated global production quantities for HFC-152a, HFC-227ea, HFC-236fa and HFC-245fa are around 170 ktonnes, of which more than 50% of the total concerns HFC-152a production (Kaixiang, 2015, Kuijpers, 2015) (the total can be translated into about 150 Mt CO2-eq. in climate terms).

Table 6-2: Estimates for global HFC production (for HFC-32, -125, -134a and -143a)

| Gg (ktonnes) for HFCs (per year) | (Montzka, 2015) Emissions year 2012 | UNFCCC based estimate for non-A5 prod. (2012) | Estimate for non-A5 production (for 2015) | Estimate from various sources A5 production (for 2015) | Estimate global production year 2015 (*) |
| --- | --- | --- | --- | --- | --- |
| HFC-32 | 16 (21**) | ≈ 22 | 23 | 71 | 94 |
| HFC-125 | 41 | < 30 | 31.5 | 98.5 | 130 |
| HFC-134a | 173 | < 100 | 97 | 161^ | 258 |
| HFC-143a | 21 | <10 | 11 | 17 | 28 |

Note: (*) Global production is equal to non-Article 5 plus Article 5 (China, minor other) production

Note: (**) Estimate from Rigby (2013)

Note: (^) New value for this report, due to the addition of the HFC-134a production quantity in one Article 5 Party

These production data for certain years are reasonably reliable global estimates and have been used in order to check the demand data determined via the bottom-up method used, where details are given in the sections below for the R/AC sector.

For the R/AC sector as a whole, the total bottom-up demand that has been calculated for the year 2015 for non-Article 5 Parties (200.5 ktonnes) and Article 5 Parties (272.9 ktonnes) equals 473.4 ktonnes. This relates to the four main HFCs given in Table 6-2. It would imply that about 37 ktonnes of HFCs (mainly HFC-134a) are used (globally) in sectors other than R/AC; these other sectors would mainly be foams, medical and technical aerosols. One needs to take into account that both the production estimates and the bottom up calculated R/AC demand have uncertainties, as mentioned above.

The value of 37 ktonnes used in sectors other than R/AC will be further investigated in the update September 2016 TF report.

## 6.4		Non-Article 5 scenarios up to 2050

### 6.4.1	BAU scenario

The figures below present the results of the Non-Article 5 scenario calculations:

- Non-Article 5 BAU scenario with subdivision for refrigerants.

- Non-Article 5 BAU scenario with subdivision for the various R/AC sub-sectors.

Figure 6-1: Non-Article 5 BAU scenario with subdivision for the various refrigerants or refrigerant blends in tonnes and ktonnes CO2-eq.

Figure 6-1 shows the current and projected future non-Article 5 refrigerant BAU demand, with a subdivision for the commonly used high-GWP refrigerants and low-GWP refrigerants. The demand is given in tonnes and in GWP weighted terms (in ktonnes CO2-eq.). The amount of low-GWP refrigerants in the BAU scenario increases rapidly after 2020, because the BAU scenario includes the EU F-gas regulation as well as the US measures that enter into force as of 2016-2021 (e.g. low GWP in manufacturing of MACs). Over the period 2010-2050, the importance of R-410A and also R-407C for stationary AC becomes more and more dominant, with an increase of a factor 2 in tonnes and in GWP weighted tonnes between 2015 and 2050.

Figure 6-2 shows the non-Article 5 refrigerant BAU demand, with a subdivision for the different R/AC sub-sectors (n.b., all graphs start in the year 1990). The demand is given in tonnes and in ktonnes CO2-eq.). By 2030-2050, stationary AC accounts for more than 80% of the GWP adjusted tonnage (even when using low growth percentages, as given in Table 6-1). This is due to the fact that only a small amount of regulatory restrictions have been built in.

Figure 6-2: Non-Article 5 BAU scenario; subdivision for the various R/AC sub-sectors

It is interesting to compare the Non-Article 5 BAU scenario without and with certain regulations; it then shows the impact of these regulations over the time period considered (in fact the values for these two types of BAU scenarios can be found in the Annexes of the XXVI/9 Task Force and this XXVII/4 Task Force report. Annex 3 gives the summary table with the regulations for the EU, USA and Japan. In the BAU scenario in this report the EU and US regulations, making certain HFCs unacceptable for certain sub-sectors by specific dates, have been applied as their impacts are very specific related to the R/AC sectors and sub-sectors.

Figure 6-3 shows the impact of regulations on the BAU demand. The demand is expected to be lower as of 2015 when certain regulations enter into force, the difference will increase after 2019-2020 when more regulations are assumed to be in place and the impact of the servicing demand becomes more visible. The difference between both types of BAU demand is in the order of 140 Mt CO2-eq. in the year 2030. The demand with regulations does not increase much between the years 2015 and 2030, after which the growth in certain commercial refrigeration subsector and particularly in the stationary AC subsector are determining.

Figure 6-3: Non-Article 5 BAU scenario without and with consideration of national and reginal regulations (without regulations until 2030; with regulations until 2050)

Figure 6-4 below is in principle the same as in the XXVI/9 report (UNEP, 2015). It is surprising that, with the assumptions used, the percentage of R-404A in manufacturing decreases sharply, servicing remains (with the assumptions on the servicing percentage) and increases again after 2033 due to economic growth. The low GWP fraction remains very moderate in ktonnes CO2-eq., but that number implies a much larger percentage in tonnes.

Figure 6-4: New manufacturing and servicing parts of the non-Article 5 BAU scenario with a subdivision for the various R/AC sub-sectors

### 6.4.2 	MIT-3 scenario

The following figures are for the MIT-3 scenario, for non-Article 5 Parties, in the various R/AC sub-sectors. This is the scenario where all sub-sectors are assumed to have converted by the year 2020. The total demand, the new manufacturing and the servicing demand are shown in Figs 6-5, 6-6, and 6-7.

Figure 6-5: Total demand for the Non-Article 5 MIT-3 scenario with a subdivision for the various R/AC sub-sectors

In MIT-3, the conversion in all sub-sectors to replace high-GWP refrigerants with a variety of refrigerants with an average GWP of 300 is assumed to be complete by 2020. Manufacturing capacity is converted in equal portions per year during the period 2017-2020. This is a major difference with the BAU scenario in which stationary AC is not addressed in this manner.

Figure 6-5 shows the steep decrease in the years before 2020, after which the curve flattens due to continued servicing needs. Since some high-GWP equipment will have been manufactured until 2020, and has an average 12 year lifetime, supplies of high-GWP refrigerants will continue to be required in decreasing amounts until about 2032.

During 2010-2015, stationary AC and commercial refrigeration demands are assumed to increase quickly (see above). With transition in new manufacturing as of 2020, high-GWP refrigerants in these sector decrease, being replaced by low-GWP refrigerants that will account for more than 80% of total demand between 2020 and 2050.

What becomes again clear here, that is that the minimum demand is reached by 2032-2033, after which the demand increases again, in particular due to growth in stationary AC.

So, there is a large improvement in climate impact, although with a GWP of 300, the large refrigerant volumes considered still have a certain climate impact.

In Figure 6-6, the new manufacturing demand for the R/AC sub-sectors for high-GWP chemicals is given. By 2020, the demand for high-GWP refrigerants in new equipment manufacture falls to < 5% of the 2019 peak.

Figure 6-6: Non-Article 5 MIT-3 scenario for new manufacturing demand for high-GWP refrigerants in the various R/AC sub-sectors in ktonnes CO2-eq. (assuming manufacturing conversion over a period of 3 years, 2017-2020).

Figure 6-7: Non-Article 5 MIT-3 scenario with the servicing demand for the various sub-sectors in ktonnes CO2-eq. (assuming manufacturing conversion over the period 2017-2020)

Figure 6-7 shows the volumes of high-GWP refrigerants that will be needed for servicing the installed equipment in the MIT-3 scenario. This varies between sectors (see table in section above) and decreases rapidly between 2020 and 2032, increases again due to economic growth after 2033.

### 6.4.3 	MIT-5 scenario

This is the scenario where, for non-Article 5 Parties, all sub-sectors are assumed to have converted by the year 2025. The total, the new manufacturing and servicing demand are shown in Figs 6-8, 6-9 and 6-10.

Figure 6-8: Non-Article 5 MIT-5 scenario by R/AC sub-sectors in ktonnes CO2-eq. (compare Figure 4-4 for MIT-3)

Figure 6-8 includes both manufacturing and servicing, and is similar to Fig 6-6 for MIT-3. Figure 6-9 shows the same data for HFCs used in new manufacturing only.

Figure 6-9: Non-Article 5 MIT-5 scenario for new manufacturing demand for the various R/AC sub-sectors in GWP weighted terms (compare Fig. 6-6 for MIT-3)

In 2020, demand for new manufacturing is at about 180 Mt CO2-eq, and demand for servicing is also at about 180 Mt CO2-eq, but after 2025, the picture becomes different. New manufacturing demand decreases to less than 30 Mt CO2-eq, whereas this value is reached around the year 2037 in servicing. This is an issue that needs to borne in mind, i.e., that servicing will be delaying non-Article 5 reductions expressed in Mt CO2-eq. After a minimum in the demand in new manufacture and service, demand will increase again after 2035-2037 (5 years later than in MIT-3), due to economic growth assumed.

Figure 6-10: Non-Article 5 MIT-5 scenario with the servicing demand for the various sub-sectors in GWP weighted terms (compare Fig. 6-7 for MIT-3)

## 6.5 		Article 5 scenarios up to 2050

### 6.5.1	BAU scenario

Figure 6-11 below shows the Article 5 refrigerant BAU demand, with a subdivision for the different high GWP refrigerants and the low-GWP ones, both in tonnes and in GWP weighted terms (in CO2-eq.).

The low-GWP refrigerants applied here are again only visible in tonnes and cannot be really seen in the scale when adjusted for GWP, shown in GWP weighted terms. In the 2020-2030 period, the high-GWP refrigerant R-404A, which is used in commercial refrigeration, becomes increasingly important in GWP weighted terms.

The demand calculated for the year 2015 is about 300 ktonnes, a higher value than calculated for the BAU demand in non-Article 5 Parties (210-220 ktonnes, see above).

Figure 6-12 shows the Article 5 refrigerant BAU demand for the different sub-sectors. The demand is again given in tonnes and in GWP weighted terms (ktonnes CO2-eq.). The BAU model predicts that between 2015 and 2050, overall demand increases by a factor of 7-8, to about 4.5 Gt CO2. Stationary AC increases substantially, but the commercial refrigeration sub-sector also is important in GWP terms, due to the use of the high-GWP R-404A.

Figure 6-11: Article 5 BAU scenario with a subdivision for the various refrigerants and refrigerant blends in tonnes and ktonnes CO2-eq.

Figure 6-12: Article 5 BAU scenario with a subdivision for the various sub-sectors in tonnes and ktonnes CO2-eq.

Figure 6-13: Article 5 BAU scenario with new manufacturing and servicing demand for the various refrigerants (both in ktonnes CO2-eq.) (note the scale difference with Figs. 6-11 and 6-12)

Figure 6-13 shows the demand for new manufacturing and for servicing. When manufacturing increases rapidly, the demand for servicing initially lags behind the volumes used for manufacturing. However, after a certain period it catches up, the servicing volumes become comparable to those used in manufacturing as follows in the BAU scenario (in ktonnes, not in ktonnes CO2-eq.):

- 2015: new manufacturing 195 kt, servicing 100 kt

- 2020: new manufacturing 300 kt, servicing 200 kt

- 2030: new manufacturing 530 kt, servicing 515 kt

- 2050: new manufacturing 915 kt, servicing 1080 kt

### 6.5.2	MIT-3 scenario

In MIT-3, as of 2020, the conversion is assumed to start in all sub-sectors to replace high-GWP refrigerants with a variety of refrigerants, with the refrigerant blends assumed to have an average GWP of 300. Conversion has been assumed to take six years for Article 5 Parties, and the manufacturing capacity is modelled to convert in equal portions per year during the period 2020-2025 (six years). The following graphs are for the Article 5 MIT-3 scenario, split into in the various R/AC sub-sectors.

Figure 6-14: Article 5 MIT-3 scenario with the demand for the R/AC sub-sectors, including both new manufacturing and servicing

Figure 6-14 shows the steep decrease in the first six years as of 2020, after which the curve flattens due to continued servicing needs only. Since some high-GWP equipment will have been manufactured until 2025, and has an average 12 year lifetime, supplies of high-GWP refrigerants will be continue to be required --in decreasing amounts-- until about 2035-37.

During 2010-2015, stationary AC and commercial refrigeration demands increase rapidly. With controls assumed on new manufacturing as of 2020, the high-GWP refrigerant demand in these sector decreases, being replaced by low-GWP refrigerants, which will account for 80% of total demand between after 2025-2030. This is a large improvement in climate impact, although with this GWP of 300, the large refrigerant volumes considered still have a certain climate impact, the relative importance of these refrigerants is now much lower in the GWP weighted graph. The demand increases again (even with a large percentage low GWP refrigerants) after 2032, due to assumed economic growth.

In Figure 6-15, the new manufacturing demand for the R/AC sub-sectors for high-GWP chemicals is given. By 2026, the demand for high-GWP refrigerants in new equipment manufacture falls to <20% of the 2019 peak value, then starts to increase again due to economic growth.

Figure 6-15: Article 5 MIT-3 scenario for new manufacturing demand for high-GWP refrigerants in the various R/AC sub-sectors in ktonnes CO2-eq. (compare Fig. 6-6 for non-Article 5 manufacturing demand)

Figure 6-16: Article 5 MIT-3 scenario with the servicing demand for the various sub-sectors in ktonnes CO2-eq. (compare Fig. 6-7 for non-Article 5 servicing demand)

Figure 6-16 shows the amounts of high-GWP refrigerants in ktonnes CO2-eq. that will be needed for servicing the installed equipment. This varies between sectors and according to the speed of the manufacturing transition (the slower the manufacturing transition, the longer the servicing tail). Amounts (expressed in GWP weighted terms) will increase again after 2030-2032.

### 6.5.3 	Impact of manufacturing conversion periods in the MIT-3 scenario

Figure 6-17 shows the demand dependent on the rate of conversion or the length of the conversion period, which is an important parameter (unchanged from what was given in (UNEP, 2015)). The six years conversion period in manufacturing for all sub-sectors results in a decrease of approximately 40% by the year 2026, and about 50% by 2030. After 2026, the remaining demand is for servicing, and only declines by about 10% over the following four years (2026-2030). At the other extreme, a twelve years manufacturing conversion period only leads to a negligible reduction by 2026, and a 25% reduction by 2030. There is a difference of about 350 Mt CO2-eq. between the 6 and 12 year manufacturing conversion periods after 2025.

Figure 6-17: Article 5 MIT-3 demand scenario for all R/AC sectors for new manufacturing conversion periods of 6-8-10-12 years in Mt CO2-eq. (UNEP, 2015)

A twelve year conversion period does not yield a lower demand until after 4-5 years after the start of the conversion in the year 2020. The build-up of the servicing demand (from the manufacturing that has not yet been converted) causes this increasing profile in the demand curve (2020-2025). Ten years after the start of the conversion in 2020, a demand reduction of 20-25% can be observed in this case. In the year 2026, the demand for the 12 years conversion period is almost twice as high as for the six years conversion period, which underscores that a rapid conversion will be very important. It will be clear that there is a direct relationship of the shape of the curves to the conversion period. There are also cost implications. A six year conversion period would imply twice the costs in the first six years after 2020 (2021-2026), compared to the 12 years conversion period, where the same amount will be spread over 12 years (see chapter 6 in the XXVI/9 Task Force report).

A longer period than 12 years, i.e., 18 years has been considered where it concerns the total demand compared to the 6 and 12 years conversion period. The various demands are given in Figure 6-18 (with also BAU demand as developing 2020-2024). The demand for a 18 years conversion period first increases (servicing build-up) then decreases after 2028-2030.

Figure 6-18: Article 5 MIT-3 total demand scenarios for 6, 12 and 18 years manufacturing conversion periods (compare also Figure 6-14 and 6-17 for MIT-3, 6 years and 6-8-10-12 years conversion periods)

Whereas the 6 and 12 years conversion periods result in a demand decrease after 2020, the 18 years conversion period yields an almost 10% increase in demand first, until the year 2030, then starts to decrease and reaches the 2020 demand level again in the year 2037.

This is due to the build-up of servicing demand from HFC products still being manufactured, while there is economic growth for the various R/AC sub-sectors. The 6 years conversion has no high GWP servicing demand after 2032-2034, the 12 years conversion has high GWP HFC servicing demand until 2042-2044, for the 18 years conversion period there is still some high GWP servicing demand until around 2050.

The demand for the period 2020-2050 for a 6 years conversion period is about 15,800 Mt CO2-eq., increases to 20,500 Mt CO2-eq. for a 12 years, and to 27,000 Mt CO2-eq. for a 18 years conversion period, a 70% increase compared to the 6 years conversion period.

### 6.5.4	MIT-4 scenario

Figure 6-19: Article 5 MIT-4 total demand scenario by R/AC sub-sectors in ktonnes CO2-eq. (compare Figure 6-14 for MIT-3)

Figure 6-19 includes both manufacturing and servicing, and is the same as Fig 6-14 for MIT-3, except for the stationary AC sub-sector graph (in green), which continues to increase until 2025, before declining. MIT-4 parameters are otherwise identical to MIT-3 (replacement refrigerant blends GWP 300; 6 year manufacturing conversion).

Figure 6-20 also shows the data for HFCs used in new manufacturing only. The various sub-sectors now decline to zero new manufacturing demand at different times.

Demand in GWP weighted terms increases again after 2030-2032.

Figure 6-20: Article 5 MIT-4 scenario for new manufacturing demand for the various R/AC sub-sectors in ktonnes CO2-eq. (compare Fig. 6-15 for MIT-3)

Figure 6-21: Article 5 MIT-4 scenario with the servicing demand for the various sub-sectors in ktonnes CO2-eq. (stationary AC starting in 2025, and assuming a conversion of manufacturing over a period of six years) (compare Fig. 6-16 for MIT-3)

In 2020-2025, demand for new manufacturing peaks at about 550 Mt CO2-eq, and demand for servicing is about 300 Mt CO2-eq, but by 2026, these values are reversed. Servicing demand peaks around 2027, at a high level of about 560 Mt CO2-eq., due to the late conversion of the stationary AC sector (assumed to rely on the refrigerants R-410A and R-407C).

The above graphs give a good impression of the impact of the stationary AC sector.

### 6.5.5	Impact of manufacturing conversion periods in the MIT-4 scenario

Figure 6-22: Article 5 MIT-4 demand scenario for all R/AC sectors combined for new manufacturing conversion periods of 6-8-10-12 years in Mt CO2-eq. (compare Figure 6-17 for the MIT-3 scenario) (UNEP, 2015)

Impact of the rate of manufacturing conversion: a long period of manufacturing conversion will result in an enhanced and long-lasting demand for high-GWP HFCs for servicing.

Fig. 6-22 gives the four curves for the six, eight, ten and 12 years manufacturing conversion periods for all refrigeration and AC sub-sectors together (as in (UNEP, 2015)). The delayed manufacturing conversion for stationary AC from 2020 to 2025 makes a large difference in the high-GWP demand.

For a six year conversion period, the HFC demand for MIT-3 and MIT-4 is projected for 2030 as (compare Figs. 6-17 and 6-22):

- MIT-3 (stationary AC conversion starting at 2020)  -  410 Mt CO2-eq

- MIT-4 (stationary AC conversion starting at 2025)  -  640 Mt CO2-eq

The delay of five years for stationary AC conversion to 2025 results in a more than 50% increase in annual HFC climate impact by the year 2030.

The MIT-4 scenario has a major adverse climate impact compared to MIT-3. There are cost implications of the MIT-4 scenario.

A delay of five years for starting SAC conversion, and a six year manufacturing conversion period, means that the overall costs have to be considered over a longer period than six years (i.e., over 12 years (rather than six years)).

### 6.5.6	MIT-5 scenario

Figure 6-23: Article 5 MIT-5 scenario by R/AC sub-sectors in ktonnes CO2-eq. (compare Figure 6-14 and 6-19 for MIT-3 and MIT-4)

Figure 6-23 includes both manufacturing and servicing, and is similar to Figs 6-14 and 6-19 for MIT-3 and MIT-4 (replacement refrigerant blends at a GWP of 300; six year manufacturing conversion).

Figure 6-24 also shows the same data just for HFCs used in new manufacturing. All sub-sectors decline to zero new manufacturing demand at the same time (as in MIT-3).

Figure 6-24: Article 5 MIT-5 scenario for new manufacturing demand for the various R/AC sub-sectors in ktonnes CO2-eq. (manufacturing conversion over a period of six years) (compare Figure 6-15 and 6-21 for MIT-3 and MIT-4)

Figure 6-25: Article 5 MIT-5 scenario with the servicing demand for the various sub-sectors in ktonnes CO2-eq. (assuming a conversion of manufacturing over a period of six years) (compare Figure 6-16 and 6-21 for MIT-3 and MIT-4)

In 2025, demand for new manufacturing peaks at about 760 Mt CO2-eq, and demand for servicing is about 650 Mt CO2-eq. After 2030, the manufacturing demand has gone down to a little more than 100 Mt CO2-eq., then increases again due to assumed economic growth to more than 200 Mt CO2-eq.

Servicing demand peaks at about 660 Mt CO2-eq., due to the late conversions of all sub-sectors, then decreases until around 2045 to about 330 Mt CO2-eq., after which year it starts to increase again (economic growth assumed).

### 6.5.7	Impact of manufacturing conversion periods in the MIT-5 scenario

Figure 6-26: Article 5 MIT-5 demand scenario for all R/AC sectors combined for new manufacturing conversion periods of 6-8-10-12 years (compare Figures 6-17 and 6-23 for the MIT-3 and MIT-4 scenarios) (UNEP, 2015)

The impact of the rate of manufacturing conversion is that a long period of manufacturing conversion will result in an enhanced and long-lasting demand for high-GWP HFCs for servicing.

Fig. 6-26 gives the 4 curves for the six, eight, ten and 12 years manufacturing conversion periods for all refrigeration and AC sub-sectors together (again unchanged from what was given in (UNEP, 2015)). The delayed manufacturing conversion for all sub-sectors as of 2025 makes a large difference. While demand for a six year conversion period decreases substantially between 2025 and 2030, a 12 year conversion period only results in a small decrease between 2025 and 2030 (about 100 Mt CO2-eq.).

For a six year conversion period HFC demand is projected for 2030 for MIT-3 and MIT-5 as:

- MIT-3 (all conversions starting at 2020)  -  410 Mt CO2-eq.

- MIT-5 (all conversions starting at 2025)  -  810 Mt CO2-eq.

The delay of five years for all sub-sector conversions to 2025 results in roughly a 100% increase in annual weighted climate impact by the year 2030.

The MIT-5 scenario has a major adverse climate impact compared to MIT-3 (and also to some degree to MIT-4). Furthermore, cost implications of the MIT-5 scenario will therefore be larger than for MIT-3 and MIT-4. In the case of a six year manufacturing conversion period, overall costs will have to be covered over six years (expansion to 12 years does not seem desirable given the climate impact numbers).

## 6.6 	Refrigerant demand and mitigation benefit numbers

On the basis of the development of the demand for the various refrigerants and their replacements for the various sub-sectors (high-GWP and low-GWP alternatives), total demand in tonnes, as well as in GWP based CO2-eq. tonnes can be calculated. The tables below extend to 2050 the non-Article 5 and Article 5 demand in tonnes and Mt CO2-eq. for BAU, MIT-3 and MIT-5 scenarios.

Table 6-3: Current and future refrigerant demand for (refrigerant) ODS alternatives (BAU scenario) for the period 2010-2050 in non-Article 5 Parties (tonnes)

|  |  |  | 2010 | 2015 |  | 2020 |  | 2025 |  |  | 2030 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| nA5 BAU | HFC-134a |  | 79,097 | 77,977 |  | 72,872 |  | 76,869 |  |  | 82,356 |
|  | R-404A + R-507 |  | 17,084 | 18,376 |  | 18,584 |  | 19,357 |  |  | 22,780 |
|  | R-407C |  | 11,195 | 26,802 |  | 34,942 |  | 43,946 |  |  | 50,402 |
|  | R-410A |  | 39,385 | 77,354 |  | 94,230 |  | 114,001 |  |  | 131,319 |
|  | Low GWP |  | 7,011 | 11,844 |  | 13,907 |  | 16,802 |  |  | 20,538 |
|  | Total |  | 153,772 | 212,353 |  | 234,535 |  | 270,975 |  |  | 307,395 |
|  |  |  | 2030 |  | 2035 |  | 2040 |  | 2045 | 2050 |  |
| nA5 BAU |  | HFC-134a | 82,356 |  | 93,316 |  | 108,107 |  | 125,265 | 145,166 |  |
|  |  | R-404A + R-507 | 22,780 |  | 26,151 |  | 30,221 |  | 34,960 | 40,470 |  |
|  |  | R-407C | 50,402 |  | 58,256 |  | 67,534 |  | 78,291 | 90,760 |  |
|  |  | R-410A | 131,319 |  | 151,966 |  | 176,170 |  | 204,229 | 236,758 |  |
|  |  | Low GWP | 17,694 |  | 21,170 |  | 25,071 |  | 29,334 | 34,188 |  |
|  |  | Total | 307,395 |  | 350,859 |  | 407,103 |  | 472,079 | 547,342 |  |

Table 6-4: Current and future refrigerant demand for (refrigerant) ODS alternatives (BAU scenario) for the period 2010-2050 in non-Article 5 Parties (ktonnes CO2-eq.)

|  |  | 2010 | 2015 |  | 2020 |  |  | 2025 |  | 2030 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| nA5 BAU | HFC-134a | 102,825 | 101,370 |  | 94,733 |  |  | 99,930 |  | 107,064 |
|  | R-404A + R-507 | 67,397 | 72,490 |  | 73,312 |  |  | 76,367 |  | 89,875 |
|  | R-407C | 18,135 | 43,419 |  | 56,606 |  |  | 71,193 |  | 81,652 |
|  | R-410A | 75,619 | 148,520 |  | 180,922 |  |  | 218,882 |  | 252,133 |
|  | Low GWP | 8 | 10 |  | 13 |  |  | 19 |  | 27 |
|  | Total | 263,984 | 365,809 |  | 405,586 |  |  | 466,391 |  | 530,751 |
| nA5 BAU | HFC-134a | 107,064 |  | 121,311 |  | 140,539 | 162,845 |  | 188,716 |  |
|  | R-404A + R-507 | 89,875 |  | 103,180 |  | 119,238 | 137,936 |  | 159,679 |  |
|  | R-407C | 81,652 |  | 94,374 |  | 109,405 | 126,831 |  | 147,032 |  |
|  | R-410A | 252,133 |  | 291,774 |  | 338,246 | 392,120 |  | 454,575 |  |
|  | Low GWP | 27 |  | 32 |  | 38 | 44 |  | 51 |  |
|  | Total | 530,751 |  | 610,671 |  | 707,466 | 819,776 |  | 950,053 |  |

Table 6-5: Current and future refrigerant demand for (refrigerant) ODS alternatives (MIT-3 scenario) for the period 2010-2050 in non-Article 5 Parties (tonnes)

| MIT-3 |  | 2010 | 2015 |  | 2020 |  | 2025 |  |  | 2030 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| nA5 3-year conversion 2020 | HFC-134a | 79,097 | 77,977 |  | 18,758 |  | 13,415 |  |  | 7,154 |
|  | R-404A + R-507 | 17,084 | 18,376 |  | 12,882 |  | 5,531 |  |  | 2,046 |
|  | R-407C | 11,195 | 26,802 |  | 13,987 |  | 10,417 |  |  | 2,716 |
|  | R-410A | 39,385 | 77,354 |  | 22,337 |  | 15,831 |  |  | 4,127 |
|  | Low GWP | 7,011 | 11,844 |  | 133,007 |  | 189,570 |  |  | 252,410 |
|  | Total | 153,772 | 212,353 |  | 200,971 |  | 234,764 |  |  | 268,453 |
|  |  | 2030 |  | 2035 |  | 2040 |  | 2045 | 2050 |  |
| nA5 3-year conversion 2020 | HFC-134a | 14,013 |  | 3,941 |  | 4,497 |  | 5,153 | 5,923 |  |
|  | R-404A + R-507 | 2,046 |  | 155 |  | 121 |  | 94 | 73 |  |
|  | R-407C | 2,716 |  | 0 |  | 0 |  | 0 | 0 |  |
|  | R-410A | 4,127 |  | 0 |  | 0 |  | 0 | 0 |  |
|  | Low GWP | 252,410 |  | 353,069 |  | 409,796 |  | 475,307 | 551,172 |  |
|  | Total | 268,453 |  | 357,165 |  | 414,414 |  | 480,554 | 557,168 |  |

Table 6-6: Current and future refrigerant demand for (refrigerant) ODS alternatives (MIT-3 scenario) for the period 2010-2050 in non-Article 5 Parties (ktonnes CO2-eq.)

| MIT-3 |  | 2010 |  | 2015 |  |  | 2020 | 2025 |  | 2030 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| nA5 3-year conversion 2020 | HFC-134a | 102,825 |  | 101,370 |  |  | 24,384 | 17,441 |  | 9,301 |  |
|  | R-404A + R-507 | 67,397 |  | 72,490 |  |  | 50,811 | 21,816 |  | 8,072 |  |
|  | R-407C | 18,135 |  | 43,419 |  |  | 22,660 | 16,876 |  | 4,401 |  |
|  | R-410A | 75,619 |  | 148,520 |  |  | 42,886 | 30,396 |  | 7,923 |  |
|  | Low GWP | 8 |  | 10 |  |  | 29,826 | 43,478 |  | 58,396 |  |
|  | Total | 263,984 |  | 365,809 |  |  | 170,568 | 130,007 |  | 88,093 |  |
| MIT-3 |  |  | 2030 |  | 2035 | 2040 |  |  | 2045 |  | 2050 |
| nA5 3-year conversion 2020 | HFC-134a |  | 9,301 |  | 5,124 | 5,846 |  |  | 6,699 |  | 7,700 |
|  | R-404A + R-507 |  | 8,072 |  | 611 | 475 |  |  | 370 |  | 288 |
|  | R-407C |  | 4,401 |  | 0 | 0 |  |  | 0 |  | 0 |
|  | R-410A |  | 7,923 |  | 0 | 0 |  |  | 0 |  | 0 |
|  | Low GWP |  | 58,396 |  | 72,898 | 84,498 |  |  | 97,948 |  | 113,542 |
|  | Total |  | 88,093 |  | 78,633 | 90,819 |  |  | 105,017 |  | 121,530 |

The following can be observed for non-Article 5 Parties and the MIT-3 scenario, which results in the conversion of manufacturing by the year 2020:

- The demand for various HFCs in non-Article 5 Parties is assumed to decrease substantially between 2015 and 2030, by more than 70% in climate weighted terms, thereafter the decrease will be much slower (values are already very low);

- The demand for the stationary AC sub-sector decreases enormously between 2025 and 2030, because virtually all requirements for high-GWP refrigerants disappear. The amount of low-GWP refrigerants in climate terms now becomes very relevant (due to the remaining GWP of 300 assumed for low-GWP refrigerant blends).

A number of tables containing the demand data in tonnes and ktonnes CO2-eq. extended to 2050 for the BAU, MIT-3 and MIT-5 scenarios in Article 5 Parties are given below.

Table 6-7: Current and future refrigerant demand for (refrigerant) ODS alternatives (BAU scenario) for the period 2010-2050 in Article 5 Parties (tonnes)

|  |  |  | 2010 | 2015 |  | 2020 |  | 2025 |  | 2030 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A5 BAU | HFC-134a |  | 54,393 | 74,524 |  | 100,162 |  | 127,267 |  | 161,107 |  |
|  | R-404A + R-507 |  | 13,085 | 36,404 |  | 63,963 |  | 111,927 |  | 167,690 |  |
|  | R-407C |  | 16,543 | 55,278 |  | 101,216 |  | 174,433 |  | 285,500 |  |
|  | R-410A |  | 40,975 | 106,661 |  | 192,770 |  | 284,682 |  | 364,845 |  |
|  | Low GWP |  | 22,430 | 29,318 |  | 39,132 |  | 51,975 |  | 69,915 |  |
|  | Total |  | 147,426 | 302,185 |  | 497,243 |  | 750,284 |  | 1,049,057 |  |
|  |  |  | 2030 |  | 2035 |  | 2040 |  | 2045 |  | 2050 |  |
| A5 BAU |  | R134a | 161,107 |  | 204,027 |  | 257,413 |  | 324,537 |  | 409,494 |  |
|  |  | R404A + R507 | 167,690 |  | 223,579 |  | 287,745 |  | 361,077 |  | 449,614 |  |
|  |  | R407C | 285,500 |  | 372,998 |  | 457,406 |  | 532,391 |  | 587,361 |  |
|  |  | R410A | 364,845 |  | 427,266 |  | 479,588 |  | 524,488 |  | 566,180 |  |
|  |  | Low GWP | 69,915 |  | 85,957 |  | 104,807 |  | 127,577 |  | 155,209 |  |
|  |  | Total | 1,049,057 |  | 1,313,827 |  | 1,586,959 |  | 1,870,070 |  | 2,167,858 |  |

Table 6-8: Current and future refrigerant demand for (refrigerant) ODS alternatives (BAU scenario) for the period 2010-2050 in Article 5 Parties (ktonnes CO2-eq.)

|  |  | 2010 | 2015 |  | 2020 |  | 2025 |  |  | 2030 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A5 BAU | HFC-134a | 70,712 | 96,880 |  | 130,210 |  | 165,447 |  |  | 209,440 |
|  | R-404A + R-507 | 51,584 | 143,511 |  | 252,168 |  | 441,229 |  |  | 661,025 |
|  | R-407C | 26,799 | 89,550 |  | 163,971 |  | 282,581 |  |  | 462,511 |
|  | R-410A | 78,671 | 204,789 |  | 370,118 |  | 546,589 |  |  | 700,502 |
|  | Low GWP | 62 | 115 |  | 203 |  | 314 |  |  | 469 |
|  | Total | 227,828 | 534,845 |  | 916,670 |  | 1,436,160 |  |  | 2,033,947 |
|  |  | 2030 |  | 2035 |  | 2040 |  | 2045 | 2050 |  |
| A5 BAU | HFC-134a | 209,440 |  | 265,234 |  | 334,637 |  | 421,897 | 532,343 |  |
|  | R-404A + R-507 | 661,025 |  | 881,313 |  | 1,134,195 |  | 1,423,289 | 1,772,283 |  |
|  | R-407C | 462,511 |  | 604,256 |  | 740,997 |  | 862,474 | 951,525 |  |
|  | R-410A | 700,502 |  | 820,350 |  | 920,809 |  | 1,007,017 | 1,087,066 |  |
|  | Low GWP | 478 |  | 601 |  | 752 |  | 940 | 1,171 |  |
|  | Total | 2,033,956 |  | 2,571,754 |  | 3,131,390 |  | 3,715,617 | 4,344,388 |  |

- The demand for various high-GWP HFCs in Article 5 Parties is (still) calculated to increase by a factor 3-4 in the BAU scenario in climate terms during 2015-2030 and by a factor of 7-8 during 2015-2050;

- The BAU scenario shows a large growth in demand for the high-GWP refrigerants  R-404A, R-407C and R-410A, mainly due to the external (economic growth) factors.

Table 6-9: Current and future refrigerant demand for (refrigerant) ODS alternatives (MIT-3 scenario) for the period 2010-2050 in Article 5 Parties (tonnes)

| MIT-3 |  |  |  | 2010 |  | 2015 | 2020 |  |  | 2025 |  | 2030 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A5 6-year conversion 2020 |  | HFC-134a |  | 54,393 |  | 74,649 | 91,265 |  |  | 48,357 |  | 39,331 |  |
|  |  | R-404A + R-507 |  | 13,085 |  | 36,679 | 58,259 |  |  | 36,123 |  | 12,751 |  |
|  |  | R-407C |  | 16,543 |  | 55,278 | 92,804 |  |  | 58,029 |  | 20,684 |  |
|  |  | R-410A |  | 40,975 |  | 106,661 | 170,273 |  |  | 65,015 |  | 18,972 |  |
|  |  | Low GWP |  | 22,430 |  | 29,318 | 87,522 |  |  | 562,500 |  | 991,332 |  |
|  |  | Total |  | 147,426 |  | 302,585 | 500,123 |  |  | 770,024 |  | 1,083,070 |  |
| MIT-3 |  |  | 2030 |  | 2035 |  |  | 2040 | 2045 |  | 2050 |  |
| A5 6-year conversion 2020 | HFC-134a |  | 39,331 |  | 39,386 |  |  | 47,809 | 57,936 |  | 70,499 |  |
|  | R-404A + R-507 |  | 12,751 |  | 2,970 |  |  | 1,576 | 3,306 |  | 5,077 |  |
|  | R-407C |  | 20,684 |  | 13,059 |  |  | 4,411 | 0 |  | 0 |  |
|  | R-410A |  | 18,972 |  | 13,467 |  |  | 4,267 | 0 |  | 0 |  |
|  | Low GWP |  | 991,332 |  | 1,244,943 |  |  | 1,528,895 | 1,808,828 |  | 2,092,281 |  |
|  | Total |  | 1,083,070 |  | 1,313,825 |  |  | 1,586,958 | 1,870,070 |  | 2,167,857 |  |

Table 6-10: Current and future refrigerant demand for (refrigerant) ODS alternatives (MIT-3 scenario) for the period 2010-2050 in Article 5 Parties (ktonnes CO2-eq.)

|  |  | 2010 | 2015 | 2020 | 2025 | 2030 |
| --- | --- | --- | --- | --- | --- | --- |
| A5 6-year conversion 2020 | HFC-134a | 70,712 | 96,880 | 117,959 | 61,810 | 49,670 |
|  | R-404A + R-507 | 51,584 | 143,511 | 227,693 | 141,897 | 50,899 |
|  | R-407C | 26,799 | 89,550 | 150,343 | 94,007 | 33,508 |
|  | R-410A | 78,671 | 204,789 | 326,924 | 124,828 | 36,425 |
|  | Low GWP | 62 | 115 | 11,394 | 123,925 | 230,156 |
|  | Total | 227,828 | 534,858 | 834,313 | 546,467 | 400,658 |
|  |  | 2030 | 2035 | 2040 | 2045 | 2050 |
| A5 6-year conversion 2020 | HFC-134a | 49,670 | 51,201 | 62,151 | 75,316 | 91,649 |
|  | R-404A + R-507 | 50,899 | 11,716 | 6,210 | 13,024 | 20,005 |
|  | R-407C | 33,508 | 21,156 | 7,146 | 0 | 0 |
|  | R-410A | 36,425 | 25,856 | 8,192 | 0 | 0 |
|  | Low GWP | 230,156 | 299,573 | 365,941 | 426,394 | 481,920 |
|  | Total | 400,658 | 409,502 | 449,640 | 514,734 | 593,574 |

The following can be observed for the Article 5 Parties, in the case of the MIT-3 scenario:

- The demand for various high-GWP HFCs in Article 5 Parties is estimated to increase by more than 50% between 2015 and 2020 in climate terms, however, it decreases again to the 2015 level in the year 2025;

- The most surprising result is that the demand in climate terms is reduced by only 20-25% in the year 2030, compared to 2015 (of course, it is much higher in the year 2020). This is due to the high growth assumed, in particular, for stationary AC, where, for all sub-sectors together, the use of replacement refrigerant blends with a GWP of 300 (at one million tonnes) is calculated to represent a climate impact of 230 Mt CO2-eq. in 2030;

- It should be realised that the proposed MIT-3 manufacturing conversion will be very demanding and the assumptions used here are based on the fact that institutional and industrial capacities can completely deal with the conversion in this timeframe.

Table 6-11: Current and future refrigerant demand for (refrigerant) ODS alternatives

(MIT-5 scenario) for the period 2010-2050 in Article 5 Parties (tonnes)

| MIT-5 |  |  | 2010 | 2015 |  |  | 2020 | 2025 |  | 2030 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| A5 6-year conversion 2025 | HFC-134a |  | 54,393 | 74,524 |  |  | 100,162 | 115,545 |  | 60,851 |  |
|  | R-404A + R-507 |  | 13,085 | 36,404 |  |  | 63,963 | 101,843 |  | 54,014 |  |
|  | R-407C |  | 16,543 | 55,278 |  |  | 101,216 | 160,942 |  | 108,166 |  |
|  | R-410A |  | 40,975 | 106,661 |  |  | 192,770 | 254,067 |  | 104,162 |  |
|  | Low GWP |  | 22,430 | 29,318 |  |  | 39,132 | 117,161 |  | 714,856 |  |
|  | Total |  | 147,426 | 302,185 |  |  | 497,243 | 749,558 |  | 1,042,049 |  |
| MIT-5 |  |  | 2030 |  | 2035 | 2040 |  |  | 2045 |  | 2050 |  |
| A5 6-year conversion 2025 |  | HFC-134a | 60,851 |  | 44,532 | 48,104 |  |  | 58,047 |  | 70,499 |  |
|  |  | R-404A + R-507 | 54,014 |  | 29,994 | 11,445 |  |  | 3,515 |  | 5,077 |  |
|  |  | R-407C | 108,166 |  | 30,160 | 21,180 |  |  | 7,194 |  | 0 |  |
|  |  | R-410A | 104,162 |  | 83,830 | 55,193 |  |  | 16,085 |  | 0 |  |
|  |  | Low GWP | 714,856 |  | 1,125,310 | 1,451,035 |  |  | 1,785,231 |  | 2,092,281 |  |
|  |  | Total | 1,042,049 |  | 1,313,826 | 1,586,957 |  |  | 1,870,072 |  | 2,167,857 |  |

Table 6-12: Current and future refrigerant demand for (refrigerant) ODS alternatives

(MIT-5 scenario) for the period 2010-2050 in Article 5 Parties (ktonnes CO2-eq.)

|  |  | 2010 | 2015 | 2020 | 2025 | 2030 |
| --- | --- | --- | --- | --- | --- | --- |
| A5 6-year conversion 2025 | HFC-134a | 70,712 | 96,880 | 130,210 | 150,208 | 79,106 |
|  | R-404A + R-507 | 51,584 | 143,511 | 252,168 | 401,490 | 213,054 |
|  | R-407C | 26,799 | 89,550 | 163,791 | 260,727 | 175,229 |
|  | R-410A | 78,761 | 204,789 | 370,118 | 487,808 | 199,992 |
|  | Low GWP | 62 | 115 | 203 | 16,637 | 166,480 |
|  | Total | 227,828 | 534,845 | 916,670 | 1,316,870 | 833,861 |
|  |  | 2030 | 2035 | 2040 | 2045 | 2050 |
| A5 6-year conversion 2025 | HFC-134a | 79,106 | 57,892 | 62,535 | 75,460 | 91,649 |
|  | R-404A + R-507 | 214,824 | 118,243 | 45,115 | 13,846 | 20,005 |
|  | R-407C | 175,229 | 48,859 | 34,312 | 11,654 | 0 |
|  | R-410A | 199,992 | 160,953 | 105,970 | 30,882 | 0 |
|  | Low GWP | 166,332 | 265,216 | 342,666 | 419,344 | 481,920 |
|  | Total | 835,483 | 651,163 | 590,598 | 551,186 | 593,574 |

In Tables 6-11 and 6-12 above, the following can be observed for the Article 5 Parties and the MIT-5 scenario:

- The MIT-5 scenario represents a much higher climate impact than the MIT-3 scenario. For the future, the question remains which scenario could or would be the most likely one that Article 5 Parties can and will follow;

- The demand for various high-GWP HFCs in Article 5 Parties is calculated to increase by a factor of 1.7 between 2015 and 2020 and by a factor 1.45 between 2020 and 2025, expressed in ktonnes CO2 eq. (this corresponds more or less to the same growth in refrigerant demand in tonnes);

- One might conclude that the proposed MIT-5 manufacturing conversion is not expected to be too demanding and that institutional and industrial capacities should be able to deal with the conversion in this timeframe, if not before. This, of course, assumes the gradual acceptance of alternatives for all sub-sectors before 2025, which seems to be definitely possible taking into account the pace of acceptance for many alternatives anticipated at present.

Table 6-13: Refrigerant demand for (refrigerant) ODS alternatives in the BAU, MIT-3, MIT-4 and MIT-5 scenarios for various periods in Article 5 Parties (n.b., in Mt CO2-eq.); the total concerns the total refrigerant demand over the period 2020-2050

| Period | 2020-2030 | 2031-2040 | 2041-2050 | Total |
| --- | --- | --- | --- | --- |
| A5 BAU A5 MIT-3 A5 MIT-4 A5 MIT-5 | 16016 | 26321 | 37874 | 80211 |
|  | 6349 | 4202 | 5257 | 15808 |
|  | 9762 | 5798 | 5540 | 21100 |
|  | 12069 | 6696 | 5719 | 24484 |

Table 6-14: Refrigerant demand for (refrigerant) ODS alternatives in the BAU, MIT-3, MIT-4 and MIT-5 scenarios for the periods 2020-2030, 2020-2040 and 2020-2050 in Article 5 Parties (n.b., in Mt CO2-eq.); in brackets the saving for the various MIT scenarios compared to BAU in that period is given

| Period | 2020-2030 | 2020-2040 | 2020-2050 |
| --- | --- | --- | --- |
| A5 BAU A5 MIT-3 A5 MIT-4 A5 MIT-5 | 16016 | 42337 | 80211 |
|  | 6349 (0,604) | 10551 (0,751) | 15808 (0,803) |
|  | 9762 (0,390) | 15560 (0,632) | 21100 (0,737) |
|  | 12069 (0,246) | 18765 (0,557) | 24484 (0,695) |

(As already presented in the XXVI/9 report (UNEP, 2015)) Table 6-13 (and 6-14) show the following (rounded) integrated total refrigerant demand for the three scenarios for the period 2020-2030 in Mt CO2-eq.:

BAU: 		16,000 Mt CO2-eq.

MIT-3:	  	  6,400 Mt CO2-eq.

MIT-4:   	  9,800 Mt CO2-eq.

MIT-5:		12,000 Mt CO2-eq.

The MIT-3 reduction from BAU of 9,500 Mt CO2-eq. represents a saving of 60%. In the case of the MIT-4 scenario, with a reduction of about 6200 Mt CO2-eq. compared to BAU, there is a saving of almost 40% from BAU. The MIT-5 reduction of 4,000 Mt CO2-eq. represents a smaller saving of 25% from BAU for this 2020-2030 period.

Values change calculated for the three scenarios in Mt CO2-eq. through 2050:

BAU: 		80,200 Mt CO2-eq.

MIT-3:	  	15,800 Mt CO2-eq.

MIT-4:   	21,000 Mt CO2-eq.

MIT-5:		24,500 Mt CO2-eq.

The MIT-3 reduction from BAU represents a saving of 80%. In the case of the MIT-4 scenario there is a savings of about 75% while the MIT-5 reduction of 56,000 Mt CO2-eq. compared to BAU represents a savings of 70% from BAU. There are still differences between the various MIT scenarios. However, the BAU demand for the entire period 2020-2050 becomes so large that the differences in reduction between the various mitigation scenarios MIT-3, -4 and -5 become less relevant.

A more reasonable estimate of the savings that can be realised via the various MIT scenarios may be the consideration of the period 2020-2040;

BAU: 		42,300 Mt CO2-eq.

MIT-3:	  	10,600 Mt CO2-eq.		75% saving compared to BAU

MIT-4:   	15,600 Mt CO2-eq.		63% saving compared to BAU

MIT-5:		18,800 Mt CO2-eq.		56% saving compared to BAU.

Another way to look at this is to analyse the trends in demand that are observed, as follows:

  - Peak values determined for the refrigerant demand increase with a later start of conversion. The peak value for MIT-3 in 2020 is about 820 Mt CO2-eq. The peak value for MIT-4 in the year 2023, with conversion of stationary AC starting in 2025, is 25% higher (at 1025 Mt CO2-eq.), whereas the peak value for demand for MIT-5 in the year 2025 is 62% higher than the one for MIT-3 (at 1330 Mt CO2-eq.).

  - For MIT-3, the average decline over a period of ten years after the peak year is 5.3% per year (from 820 down to 390 Mt CO2-eq. in 2030), for MIT-4 it is 4.5% per year (from 1025 down to 570 Mt CO2-eq. in 2033) and for MIT-5 it is 5.5% per year (from 1330 down to 605 Mt CO2-eq.). If the freeze year (which coincides with the peak year) is chosen as the starting point, an average annual reduction of 5% in total demand (manufacturing and servicing) seems feasible for all types of scenarios. These values all apply to a manufacturing conversion period of six years.

  - For each separate Article 5 country the peak (freeze) values will still be in the same years for the various MIT scenarios considered, however, annual reduction percentages achievable thereafter may be significantly different per country.

## 6.7		References

Campbell, 2015	Campbell, N., Presentation at OORG meeting World Bank, “HFC Production and Demand”, May 2015

IPCC, 2007		AR4, IPCC Fourth Assessment Report, 2007

Kaixian, 2015	Kaixian, W., Presentation at OORG meeting World Bank, “HCFCs/HFCs Production in China”, May 2015

Kuijpers, 2015	Kuijpers, L., Private communications from chemical manufacturers, May-July 2015

McCulloch, 2015 	Private communications with L. Kuijpers, May 2015

Montzka, 2015	S. A. Montzka, M. McFarland, S. O. Andersen, B. R. Miller, D. W. Fahey, B. D. Hall, L. Hu, C. Siso, and J. W. Elkins, Recent Trends in Global Emissions of Hydrochlorofluorocarbons and Hydrofluorocarbons: Reflecting on the 2007 Adjustments to the Montreal Protocol, J. Phys. Chem., dx.doi.org/10,1021/jp5097376, 2015

Rigby et al., 2013  	M. Rigby, R.G. Prinn, S. O’Doherty, B.R. Miller, D. Ivy, J. Muehle, C.M . Hart, P.K. Salameh, T. Arnolds, R.F. Weiss, P.B. Krummel, L.P. Steele, P.J. Fraser, D. Young and .P. Simmonds, “Recent and future trends in synthetic greenhouse gas radiative forcing”, Geophysical Research Letters, 10,1002/2013GL059099

RTOC, 2010	UNEP, Refrigeration, AC and Heat Pumps Technical Options Committee, 2010 Assessment Report, ISBN 978-9966-20-002-0

UNEP, 2015	UNEP, Update Report of the XXVI/9 TEAP Task Force, September 2015, ISBN 978-9966-076-14-4

# 7	List of acronyms and abbreviations

AHRI	Air Conditioning, Heating and Refrigeration Institute

AREP	Alternative Refrigerants Evaluation Program

ASHRAE	American Society of Heating, Refrigerating and Air Conditioning Engineers

ASTM 	American Society for Testing and Materials

CEN 	European Committee for Standardisation

CFC 	Chlorofluorocarbon

CO2 	Carbon Dioxide

COP 	Coefficient of Performance

EPA 	US Environmental Protection Agency

EU 	European Union

GWP 	Global Warming Potential

HC	Hydrocarbon

HCC	Hydrochlorocarbon

HCFC 	Hydrochlorofluorocarbon

HCFO	Hydrochlorofluoroolefin

HCO	Oxygenated hydrocarbon

HFC 	Hydrofluorocarbon

HFO 	Hydrofluoroolefin

HTOC 	Halons Technical Options Committee

IIR	International Institute for Refrigeration

IPCC 	Intergovernmental Panel on Climate Change

ISO 	International Organisation for Standardisation

LCA	Life Cycle Analysis

LCCP	Life Cycle Climate Performance

MBH	Thousand BTUs per Hour

ODP 	Ozone Depletion Potential

ODS 	Ozone Depleting Substance

OEL	Occupational Exposure Limit

R/AC	Refrigeration and Air Conditioning (also RAC&HP)

RTOC	Refrigeration, AC and Heat Pumps Technical Options Committee

SNAP 	Significant New Alternatives Policy

TEAP 	Technology and Economic Assessment Panel

TEWI	Total Equivalent Warming Impact

TLV	Threshold Limit Value

UL 	Underwriters Laboratories Inc.

UNEP	United Nations Environment Programme

VOC	Volatile Organic Compound

# Annex 1 - Summary of Informal Discussion on the TEAP Decision XXVII/4 Task Force Report for OEWG-37

Parties provided comments on this report and suggestions for TEAP’s second report under Decision XXVII/4 in an informal discussion session with TEAP, Thursday 7 April, 1-2.30 p.m. The comments and suggestions are summarized below. All these comments will be taken into consideration by the TEAP XXVII/4 Task Force within the timeline remaining to the Task Force to complete its second report for submission to OEWG-38.

Update on refrigerants

- The report should include updates and information on not-in-kind (NIK) technologies.

- Further consideration should also be provided with regards to safety with the aim of advancing technologies to meet the current safety standards in relation to the new alternatives. With regard to servicing, the report should address whether use of the alternatives including flammables would require specialized training, including under HAT conditions.

- A request was made for addressing criteria from paragraph 1(a) of the previous Decision XXVI/9, including addressing whether alternatives are “environmentally sound” in order to avoid having to revisit in the future decisions that are made today in selecting alternatives. Additionally, the term “environmentally sound” could be further elaborated.

Testing of alternatives under high ambient temperature (HAT) conditions

- A Party that had proposed language for considering a HAT exemption in the contact group meeting offered to share the information to TEAP on the criteria and data used; the party also noted that it would welcome other alternative approaches.

- The section in the report that discussed the results of the alternatives testing under HAT conditions were actually positive, and this positive outcome along with any negative outcomes of the testing should be better reflected in the executive summary of the report. However, the executive summary of the report should also indicate that certain elements were not included in the alternatives testing such as risk assessment.

- The cost element should be reflected in a contextual manner to include the cost of in-kind replacement, full or partial system redesign.

- A couple of Parties suggested that it would be helpful if the report could include an overview of the status of the various alternatives based on the testing - not in additional discussion within the report but perhaps in a table format so key information would be in one place.

- A Party asked for HAT considerations to include some additional uses including in industrial equipment, chillers, and other sub-sectors such as transport air conditioning; additional uses mentioned were cooling of mines in South Africa and propane-driven technologies in Australia.

Scenarios

- A Party identified that some idea of the magnitudes of the present banks of HFCs would be helpful.

- A request was made on whether the TEAP reported annual production of HFCs could be provided by countries.

- A Party suggested that the report should clarify that only certain HFCs were included in the production figures.

- With regard to the BAU, not all existing regulations were used so TEAP was requested to investigate whether the report could further consider these in addition to a number of corporate commitments and changes in national procurement regulations.

- A Party requested whether the report could show a BAU scenario without any regulatory actions incorporated.

- Further clarification is needed on the estimated growth rates that were used compared to refrigerant demand growth.

- A request was made as to whether the impacts of a longer manufacturing conversion period of 18 years could be calculated and incorporated.

- The previous XXVI/9 report included estimated costs and emissions reductions for the various mitigation scenarios; a request was made to include these costs and benefits into this XXVII/4 report.

- A party requested whether the scenarios could show the demand on a regional basis.

# Annex 2 - Background information about refrigeration in the fishing industry

## A2.1		The fishing industry

The total number of fishing vessels in the world in 2010 is estimated at about 4.36 million, which is similar to previous estimates. Of these, 3.23 million vessels (74%) are considered to operate in marine waters, with the remaining 1.13 million vessels operating in inland waters. Overall, Asia and the Pacific have the largest fleet, comprising 3.18 million vessels and accounting for 73% of the world total, followed by Africa (11%), Latin America and the Caribbean (8%), North America (3%), Europe (3%) and rest of world (2%). Globally, 60% of all fishing vessels were engine-powered in 2010, but although 69% of vessels operating in marine waters were motorised, the figure was only 36% for inland waters. For the fleet operating in marine waters, there were also large variations among regions, with non-motorised vessels accounting for less than 7% of the total in Europe and the Near East, but up to 61% in Africa (UN, 2010).

As shown in Figure A2-1, almost 80% of the motorised fishing vessels in the world are less than 12m in overall length (LOA). Such vessels dominate in all regions, but markedly so in Africa, the Near East, and Latin America and the Caribbean. About 2% of all motorised fishing vessels correspond to industrialised fishing vessels of 24 m and larger (with a gross tonnage (GT) of roughly more than 100 GT or 100 Gross Register Tonnage (GRT)) and that fraction was larger in the Pacific and Oceania region, Europe, and North America.

Figure A2-1 Ship Length (FAO, 2014)

### A2.1.1	Pacific fishing vessels

The area described as the Pacific Islands is shown in the Figure A2-2 below.

Marine Fisheries is the single largest industry and source of income for many Pacific Island Countries (PICs) (Awira, 2014). Economic benefit derived from this sector is sourced through a direct involvement of PICs in fishing, fish processing and through the licensing arrangement between PICs and foreign fishing nations. Many different nations operate fishing vessels in the PIC region and refrigeration is essential in all stages of the fisheries industry: from catching to processing to the consumer. Although PICs are complying with their obligations under the Montreal Protocol on the phasing out of HCFCs, this sector is still an elusive area. The demand and market supply routes of refrigerants and refrigerant servicing in the marine fishing sector is not known for PICs and perhaps for other regions.

The management of Ozone Depleting Substances (ODS) in the fishing sector has to be intimately aligned with the complex nature and magnitude of this industry including that of clarifying the responsibility of flag states and vessels owners in the context of sustainable development. As of June 2014 the number of vessels registered under the Pacific Islands Forum Fisheries Agency (FFA), Good Standing Register stands at a total of 1,332 vessels (FFA database 2014) including bunkers, fish carriers, long liners, mother ships, pole and liners and purse seiners. Out of this total, the vessels with cold storage capabilities that have a direct link to the consumption of refrigerants with ozone depleting properties are long liners, purse seiners, fish carriers and pole and line fishing vessels.

One may ask why there are so many vessels operating in the region vying for the same four species of tuna? The answer is that the tuna fishery in the waters of the FFA member countries is the largest in the world and there is a need to generate and maximise economic benefit from fishery resources for PICs, as for some this is the only resource they have. Ten years ago, income from fisheries access was around US$ 40 million but now PICs are getting somewhere around US$ 250 million in fishing revenue and other direct benefits. This shows an increase of over 500% which can be attributed to the management measures put into place by FFA and the Tuna Commission as well as the introduction of the Parties of the Nauru Agreement vessel day scheme in 2007. In 2013 the total catch of tuna resources from the Western and Central Pacific - Commission Area (WCP-CA) was 2.61 million tonnes and this is valued at US$ 6.3 billion. Catch taken from waters of the FFA member countries is 1.56 million tonnes or 60% of the WCP-CA total and this is valued at US$ 3.4 billion.

Figure A2-2 Map showing Pacific Islands region (Gillet, 2011)

With more than 1,000 vessels roaming the Pacific Ocean from various nationalities fishing for tuna, there is an urgent need to have mechanisms to monitor and control the consumption of all refrigerants used on fishing vessels to ensure that PICs meet their obligations under the Montreal Protocol and the International Maritime Organization’s (IMO) agreement on the prevention of air pollution from ships which is covered under MARPOL 73/78 Annex VI. FFA Members do not have this capacity, nor do they have the financial, human or institutional resources. Monitoring, reporting and enhanced enforcement of refrigerant supplies to fishing vessels is also recommended. Often the fishing vessels enter and received supplies at designated fish depots. The level and adequacy of customs controls at these ports need to be studied.

Effective enforcement of supplies to vessels can also support control requirements on illegal, unreported and unregulated (IUU) fishing. Previously published IUU loss estimates for the Western and Central Pacific region are somewhere in the region of US$ 750 million to US$ 1.5 billion a year. Where IUU involves vessels not already licensed in the fishery, it can be assumed that for IUU there will also be a high demand for refrigerants and that they may be traded illegally to meet the demand of illegal fishers. This also extends the subject of application of for example Decision XIX/12: Preventing illegal trade in ozone-depleting substances.

The distribution of ship types is shown in Figure A2-3.

Main fishing methods are Purse Seine and Long Line. Out of 1270 ships, 77% were flagged with flagged outside the area and only 23% were FFA flagged (Awira, 2015)

The biggest part of the Pacific Purse Seine, Bigeye Tuna are caught around the equator +/-10° degrees (see Figure A2-4). This means that a significant distance has to be travelled and that the fish have to be kept refrigerated or alive until landing to avoid spoilage (Honolulu, 2015).

A variety of methods are used for freezing tuna including air blast cooling or immersion in brine. Plate freezers are not generally used for larger fish due to the difficulty of getting them to fit between the plates.

One of the requirements for freezing the fish is related to parasite kill in the fish. According to European Union regulations, freezing fish at -20°C for 24 hours kills parasites. The U.S. Food and Drug Administration (FDA) recommends freezing at -35°C for 15 hours, or at                    -20°C for 7 days.

Figure A23-3 Ship types in Pacific Islands Countries (Awira, 2015)

Figure A2-4 Distribution of tuna catch

Not all fish is for export and much is used in the local economy. Industrial-scale shrimp fisheries, for instance, only occur in Papua New Guinea.

Costal fishing is very important for the local economy and nutrition, but in the global market it is only a small part of the total production. In any case these smaller boats usually use ice whereas the larger ships have mechanically refrigerated holds.

Coastal fishing in the region can be placed mostly into the following categories:

- Small-scale commercial fishing, (also referred to as “artisanal”) which can be further broadly sub-divided into those supplying domestic markets, and those producing export commodities.

- Subsistence fisheries, which support rural economies and are extremely important to the region’s nutrition and food security (Gillet, 2011)

The cold chain is not a concept implemented globally. The food spoilage in this part of the world is relatively high, in part due to the high ambient temperatures. There are numerous other techniques for storing non canned fish such as smoking, drying, brining and dry salting which do not involve refrigeration.

### A2.1.2	The EU fishery fleet

Considering that more than 70% of fishing fleet operating in the Pacific Islands is flagged outside the area (Awira, 2015), a look to the situation of other fleets is worthwhile. As an example of how the fishing fleets of non-Article 5 Parties are organised, the European Union (EU) fishery fleet situation is described here.

The EU fleet is very diverse, with the vast majority of boats being no more than 12 metres long, with a small number of vessels exceeding 40 metres in length.

Reducing fleet capacity is an essential tool for achieving a sustainable exploitation of fisheries resources. That is why the EU’s fishing fleet capacity has declined steadily since the early 1990s, in terms of both tonnage (an indicator of fish-holding capacity) and engine power (an indicator of the power available for fishing gear). The size of the EU-28 fishing fleet has dropped to about 86’500 vessels in 2013 compared to 104’000 vessels for the EU-15 in 1995, although it increased by 7.2 % between 2012 and 2013, following Croatia’s EU accession. The EU’s fishing fleet in 2013 had a combined capacity of 1.7 million gross tonnes and a total engine power of 6.6 million kW.

Almost one fifth (18.3%) of the EU-28’s fishing fleet is registered in Greece. Generally however, these Greek vessels are small, with an average size of 4.9 gross tonnes (much less than the EU-28 average of 19.2 gross tonnes) and an average engine power of 28.9 kilowatts in 2013 (compared with an EU-28 average of 76.0 kW). In terms of capacity, Spain, France, Italy and the United Kingdom had the largest fishing fleets, accounting for 54.2 % of gross tonnage and 55.8 % of engine power in 2013 (EUROSTAT, 2014).

## A2.2		Refrigeration within the fishing industry

### A2.2.1	Refrigeration on board

In order to avoid spoilage and increase shelf-life, fish must be kept refrigerated as soon as they are caught.

If the fish are caught for local use, ice is the best suited refrigeration medium, as it can be used without any machinery on board ships and provides cold storage. Ice is very well suited for fish, as i) it provides the quick cooling after harvesting, needed for good quality, ii) its temperature is just right for short term conservation, and iii) though melt water can affect the quality of other goods, it does not alter the quality of fish, which are protected by skin and scales.

If not consumed fresh, fish is processed for conservation. This yields the different products that can be found on markets: canned, frozen, freeze dried or cured. Industrial processing of fish can be done on board factory ships or in land based plants. In all cases the process is similar to other kinds of food processing, with just some peculiarities which will be pointed out later on (de Larminat, 2015).

Table A2-1 summarizes the type of conservation method for the fish depending on the type of catch and on the type of vessel used for the catch.

Table A2-1 Type of fish conservation used depending on the catch (de Larminat, 2015)

| Catches | Conservation method |
| --- | --- |
| local | ice |
| mid-distance | brine freezing/RSW |
| long-distance | deep freezing |

The smallest ships have no refrigeration at all aboard. When a little larger, they load up flake ice every morning from the harbour. The catch is then iced as it comes on-board and held cold with the ice. Larger ships have Refrigerated Sea Water (RSW) tanks and produce ice on-board. Only the largest vessels have complete factory installations with blast freezers, plate freezers, RSW tanks and ice-machines.

In recent decades, major innovations in refrigeration, ice-making, packaging and transportation to ensure product integrity have also allowed an expansion of fish distributed in fresh, chilled and frozen forms. Developing countries have experienced a growth in the share of fish production utilised as frozen products (24% of fish for human consumption in 2012, up from 20% in 2002 and 13% in 1992).

However, many countries, especially those with less-developed economies, still lack adequate infrastructure and services including hygienic landing centres, electricity, potable water, roads, ice, ice plants, cold rooms and refrigerated transport. These factors, associated with tropical temperatures, result in high post-harvest losses and quality deterioration, with subsequent risks for consumers’ health. In addition, fish marketing is also more difficult owing to often limited and congested market infrastructure and facilities. Due to these deficiencies, together with well-established consumer habits, fish in developing countries is commercialised mainly live or fresh soon after landing or harvesting, or it is processed using traditional preservation methods, e.g. salting, drying and smoking. These methods remain prevalent in many countries, in particular in Africa and Asia, which show higher proportions of cured fish compared with other continents (FAO, 2014).

### A2.2.2	Ice plants and Refrigerated Sea Water (RSW)

The ice plant is a complete installation for the production and storage of ice, including the icemaker itself together with the associated refrigeration machinery, harvesting and storage equipment, and infrastructure.

Other than by description of the ice produced, there is no simple way to classify the different types of ice makers; hence we have block, slice, plate, tube, slush ice and so on.

Typically, ice plants are vapour compression refrigerating plants able to produce up to 10 tons per hour with evaporating temperatures ranging from -10°C to -30°C.

Ice can also be produced from sea water: when seawater is frozen slowly, freshwater ice crystals are initially frozen out of the mixture. The whole solution will not be frozen until the temperature has reached -22°C, the eutectic point (the eutectic point is a physical constant for a mixture of given substances). At higher freezing rates, the ice crystals will be salt-contaminated from the very beginning but this salt will eventually migrate to the outer surface and separate during storage. As the crystals are made mainly of fresh water, the residual liquid will contain an ever increasing concentration of salt as the temperature is reduced. The special structure of seawater ice gives it different properties from freshwater ice. Seawater ice is rather soft and flexible and, at normal subcooled ice temperatures of -5 to -10°C, it will not keep the form of flakes; in fact, at -5°C, seawater ice will look rather wet. For this reason, seawater ice is usually produced at lower temperatures than freshwater ice, and often this adjustment has to be made to the ice maker. Otherwise the plant required is basically the same.

A number of ice plants are suitable for operation at sea with little modification to their design and they may use either fresh or seawater supplies. Many vessels which process their catch at sea have ice makers installed for cooling the fish during processing. Since they are often at sea for many months at a time, it would be unreasonable for them to carry ice from a shore-based plant. Some fishing vessels have ice plants installed where it may not be economical to have a permanent shore-based plant; for example, because demand for ice is only seasonal due to the type of fishery.

Other fishing vessels operate their own ice plant because of difficulties in getting regular supplies without incurring unacceptable delays in port

There are other ways of chilling fish besides using ice. For example, they can be immersed in chilled water or cold air can be blown over them. Sea water, cooled by mechanical means, RSW or by the addition of ice, Chilled Sea Water (CSW), is a suitable alternative means of rapidly chilling large quantities of whole small fish, especially on board a fishing vessel. (Graham, 1992)

### A2.2.3	Freezer trawlers

Freezing facilities are generally only installed on larger stern trawlers; these are 65m to 80m in length and have a freezing capacity of between 30 and 60t each day and a cold storage capacity of 300 to 800t.

Once the fish are aboard it is important to process and freeze them before rigor mortis sets in which, if it occurs, will result in a degradation of quality. The onset depends on time and temperature.

The first operation is to gut the fish. If they are not gutted, when the fish are thawed they produce bloodstained fillets with off flavours. It is possible to freeze them with guts but only after bleeding which solves some flavour issues but can lead to other spoilage problems.

If fish are gutted, then they still need to be bled for about 15-30 minutes and then washed before being frozen in chilled seawater. If this is not done, the blood is forced into the flesh by the freezing process, resulting in staining. Also, if the time before gutting is in excess of six hours, the blood becomes thicker and harder to wash away.

White fish should be frozen as quickly as possible but if there are limitations to freezing capacity, it is possible to store cod in ice for 3 days, haddock 2 days and hake just 1 day without serious deterioration in quality.

The layout of each factory deck on a freezer trawler, favoured in the Atlantic, will vary depending on its shape and also whether filleting takes place or white fish are frozen. However, the basic configuration will remain the same: a hatch to supply caught fish, a pound to store the fish, a gutting area, a washing area, freezing equipment and a cold store.

A freezer trawler is usually fitted out with a number of vertical plate freezers. Vertical plate freezers are hollow plates made up of sections of extruded alloy and are connected via flexible hoses to the refrigerant supply header. The cooling liquid, refrigerant or heat transfer fluid, is circulated by a pump; there is also a system for heating in order to release the plates once the fish are frozen.

Fish are packed between the plates head to tail, without gaps, any gaps make freezing slower and make fish susceptible to breakage.

Large fish should not be forced between the plates but placed into an air blast freezer. The freezing time will be dependent on the air temperature and velocity.

Plate freezers should be loaded in rotation or the freezing time will be longer due to cooling capacity limitations. If they are loaded at the same time, initially the plant demand will be very high but when the freezing is nearly complete the cooling plant will have little load.

Freezing times should never be cut short: if the blocks are removed too early they may appear hard but the middle of the fish will be soft. When they are placed in the cold store, they are likely to stick together and, worse, the store temperature will rise and the fish freeze slowly with a consequent reduction in quality. Another negative aspect is that if the fish stick together they are liable to being broken when removed.

Once the fish are frozen they are transferred to the cold store via a hoist. The cold storage temperature on trawlers is normally -40°C. (Awira, 2015)

### A2.2.4	Ultra-low temperature freezing

Even if it represents a niche within the fishing industry, the catch to be forwarded to sashimi and sushi markets deserves a mention here because it poses a technological challenge to the refrigeration industry: tunas to be consumed as sashimi or sushi must in fact be brought down to at least -60°C, after removing gills and guts, to maintain the quality grade needed for raw consumption. (The Pacific Community)

The technological challenge lies in the fact that most of the systems and refrigerants used in traditional freezing plants are not able to go down to -60°C, so particular refrigeration systems and/or refrigerants have to be implemented to achieve this goal.

Tuna is quickly bled, processed and frozen before rigor mortis sets in which is why it is said to be "fresher than fresh". Approximately 80% of tuna sold in the Japanese market is in this category and commands a high price. Only certain fish are suitable for sushi. Only if “they have the special look and glow in the eyes” are they are sent to the -60°C blast freezer. Much of the remainder goes for canned tuna production.

Varieties of fish other than tuna are also sold for sushi, and are frozen at very low temperatures before consumption (Pachai, 2013). Such treatment ensures the flavor and texture of the flesh stays at its best. However, not all fish are suitable and are also dependent on seasonal variations. In some cases such low-temperature freezing causes physiological disorders to develop within the fish. Therefore an in-depth knowledge is essential for the correct processing for the species being caught.

## A2.3		Refrigerants currently used

### A2.3.1	Refrigerants used on board

From the field experience and estimates, it is known that in 2016 about 70% of the fleet still used HCFC-22 as their main refrigerant; this is a global phenomenon and includes all seagoing vessels. Ammonia (R-717) is the second refrigerant of choice. An EU report (Faber, 2009) shows that this is also the case in Europe.

A number of different refrigerants were used on board ships in the past including ammonia. Examples of these were CFC-12, R-502 and in some cases CFC-13, this is of significance when bearing in mind the age of some of the fishing vessels (30 years old). HCFC-22 came after the above refrigerants.

Low temperature air blast coolers are either cascade or two-stage sub-atmospheric systems. Cascade systems are likely to use R-23 in their low stage.

From reported data (Awira, 2015), it is known that refrigerant charges are estimated to be about 230 to 250 metric tonnes of HCFC-22 for fish carriers, long line and purse seiner vessels chartered and flagged in FFA member Countries.

The same report states that the total HCFC refill for flagged and chartered vessels amounts to 714 metric tonnes, while the Montreal Protocol HCFC baseline (consumption) for the 14 Pacific Islands Countries amounts to 271.69 metric tonnes.

### A2.3.2	Refrigerants used on land operations

In land based industrial systems for food processing, including the fishing industry, R-717 is already the dominant refrigerant in non-Article 5 Parties while HCF-C-22 is the refrigerant mostly used by Article 5 Parties, both for process cooling and large ice plants. (de Larminat, 2015).

In recent years, non-Article 5 Parties have seen an increasing use of R-404A, especially in small and medium systems including those used for producing ice.

### A3.3.3	Refrigerant leakage

In the maritime sector, the emission factor due to leakage in air conditioning and refrigeration systems with direct expansion are very high, estimated at 40% of the charge per year. Even when indirect systems are utilised, a loss of 20% per year is common. This is due to a combination of the age, the technology and the constant vibration and racking that a ship endures (FRDC, 2013)

As already mentioned, many vessels have licenses to operate in Article 5 Parties even though their flag is not Article 5. It is then not uncommon that the systems are refilled with refrigerant origining from an Article 5 Party. This refrigerant should be reported as export and import in the flag country and not, as currently occurs, as used by the Article 5 Party. For European flagged ships it would basically be illegal to top up the charge even if operating in an Article 5 Party.

### A2.3.4	High ambient temperatures (HAT)

The issue of High Ambient Temperatures (46-52°C) is less likely to apply to fishing vessels and land based fisheries as refrigeration systems are generally cooled by sea water. Therefore, this is not very often a problem in open sea, but can become an issue in more slow moving rivers and lakes and potentially in ports where the water temperature can increase. For the refrigeration system it means that you can reach the limits of the operational envelope with the risk of the safety valve opening blowing out the refrigerant. This is mainly a problem if the ship is designed for colder water and is migrated to warmer waters for any reason. It is primarily a design topic more than a refrigeration issue.

High ambient temperatures are only significant as fish have inherently a high bacterial loading and can spoil quickly if not subject to the correct storage conditions.

## A2.4		Low-GWP alternatives to ODS refrigerants

The most important information that can be drawn from the background analysis of the fishing industry is that, currently, the existing fishing fleet is dominated by HCFC-22 and R-717.

R-717 is a non ODS substance with a low GWP and is perfectly satisfactory for continued use, once the safety issues are taken into account (R-717 is a B2L fluid according to ASHRAE 34 standard).

HCFC-22 is an ODS and must be phased-out. Substitution of HCFC-22, considering its ubiquitous presence throughout the industry, is the real challenge facing the fishing industry.

Considering also that 70% of the global fishing fleet is based in Asia/Pacific, this challenge becomes even more important for Asia/Pacific Parties and specifically for Pacific islands, whose economy is heavily dependent on their fishing industry.

Table A2-2 provides the main characteristic of all the refrigerants that can play an interesting role in HCFC-22 substitution.

### A2.4.1	Alternatives to HCFC-22

Traditionally, trawlers operate with direct expansion and have relatively high refrigerant charges and high leakage rates; this makes the choice for the transition from HCFC-22 a difficult one.

An obvious retrofit replacement for HCFC-22 is R-404A which is a very popular and widely used blend. However, due to its high GWP value, it is now being phased out in Europe by 2020, as well as in certain sub-sectors in the USA; in other regions R-404A is under pressure. Analysing the options left after the HCFC phase-out and considering that high GWP is an issue as well, one presently stands with a limited number of potential alternatives even without considering the cost implications. A non-exhaustive list of potential alternative refrigerants is shown in Table A2-2 (UNEP, 2014, UNEP, 2016).

The (unsaturated - olefin type) HFO refrigerants are not suitable to replace HCFC-22 or R-404A for low temperatures. More promising are those refrigerant mixtures obtained by blending HFC and HFO in suitable proportions to make them a low-GWP fluid and, at the same time have the properties needed for a refrigerant in this application.

Ammonia (R-717) is very competitive but requires a refrigeration plant change and cannot be considered as a retrofit.

As the situation of HCFC-22 substitutes showing low-GWP properties is rapidly and positively evolving towards the development of suitable alternatives for most of the terrestrial applications (UNEP, 2015, UNEP, 2016), one can expect that those alternatives will be suitable also for on board applications of the fishing industry.

When evaluating the substitution of HCFC-22 for on board refrigeration, the decision must take into account several variables; in principle it is possible to distinguish among the following cases:

Table A2-2 Potential HCFC-22 alternatives, their GWPs and safety class

| Refrigerant | Normal Boiling Point (°C) | GWP 100 years | Safety Class |
| --- | --- | --- | --- |
| HCFC-22 | -40.8 | 1810 | A1 |
| HFC-23 | -82,0 | 12500 | A1 |
| R-404A | -46.6/-45.8 | 4200 | A1 |
| R-407A | -45.2/-38.7 | 2100 | A1 |
| R-407C | -43.8/-36.6 | 1700 | A1 |
| R-407F | -46.1/-39.7 | 1800 | A1 |
| R-428A | -48.3/-47.5 | 3700 | A1 |
| R-448A | -45.9/-39.8 | 1300 | A1 |
| R-449A | -46.0/-39.9 | 1300 | A1 |
| R-507A | -47.1 | 4300 | A1 |
| R-717 (NH3) | -33.3 | 0 | B2L |
| R-744 (CO2) | -78* | 1 | A1 |

*Sublimation point in atmosphere of CO2. Triple point is -56.2°C@5.2 bar.

** Even if it classified of lower-toxicity (A1) it can present human health hazards when operating in enclosed spaces such as vessels: such risks have to be prevented with specific safety measures (it should be noted though, that these risks are present also with HCFC,HFC, HFO and HCFO refrigerants).

- If the entire vessel is approaching the end of its operating life and is going to be retired soon, then no refrigeration plant upgrade is worthwhile. Before going to the scrapyard, proper recover of remaining refrigerant is the most important operation to be scheduled for the refrigeration plant.

- If the ship has a long life ahead but the refrigeration plant needs a major overhaul, then the change of refrigerant is a reasonable operation to be implemented. The new refrigerant has to be chosen with care. Change of refrigerant may involve a complete refurbishment of the refrigeration plant: converting an halocarbon plant to ammonia, for example, will require disposing of all copper-nickel equipment and substitution with steel (often with stainless steel because of sea water).

- If the HCFC-22 equipped refrigeration plant is relatively young (less than 10-15 years) then retrofitting it with a drop-in solution can be the right option. Rapidly evolving situations in the development of low-GWP HFO/HFC blends makes it highly probable that in a few years a satisfactory solution also for this specific problem could be at hand.

- For new ships, several options are available nowadays: all of them are environmentally benign in terms of ozone depletion and climate change and are also economically feasible.

In the following a number of feasible options for the main applications of fishing vessels refrigeration will be described and critically analysed. At the end of the paragraph a summary table (FRDC, 2013) is provided to allow for comparisons. A separate paragraph will then be devoted to Ultra-low temperature applications, which require particular technology.

### A2.4.2	Option 1 – Non-halocarbon refrigerants (R-717 and R-744)

Ammonia (R-717) and carbon dioxide (R-744) (so called “natural” refrigerants) are fit, from a thermodynamic point of view, for the refrigeration plants aboard fishing vessels.

Ammonia is lower flammable and toxic: its application requires considerable safety requirements (sensors and alarms, ammonia concentration meters, extensive signage, training, breathing apparatus etc.) and the systems must be run by skilled personnel. Carbon dioxide is non-flammable, colourless, odourless and tasteless. Even if it classified of lower-toxicity (safety classification A1 according to ASHRAE standard 34) it can present human health hazards when operating in enclosed spaces such as vessels: such risks have to be prevented with specific safety measures (it should be noted though, that these risks are present also with HCFC and HFC refrigerants) (FRDC, 2013).

When the safety issues can be properly addressed and skilled personnel is available, then a R-717 plant can be the right choice, from both technical and economical points of view.

When safety may become an issue, the main priority is to reduce the mass of R-717 charged in the plant: confining ammonia only in one machine room, for example, can reduce the safety requirements considerably. This can be done by adopting a NH3/CO2 (R-717/R-744) cascade system: ammonia is the high-temperature fluid and carbon dioxide is the low-temperature fluid. The high-temperature side of the plant is confined to the machine room while the low temperature fluid is sent to all the plant terminals throughout the ship (Kawamura, 2015).

One of the first NH3/CO2 (R-717/R-744) cascade systems was presented in 2003 at the IIAR conference (Nielsen, 2003). The paper describes a 75m long purse seiner with a freezing capacity of 210 tons of fish per day. The system consists of 11 vertical plate freezers, a vertical flake ice freezer, and CO2 air-coolers for 3 cargo holds.

A cascade system is very efficient for low temperature operations (down to -48°C). It is also cost effective, as compressors and piping are small if compared to those needed for other fluids. Moreover, sending to the plant terminals R-744 instead than R-717 reduces the risks due to flammability and toxicity (de Larminat, 2015).

Also on board ships, the use of R-744 as the sole refrigerant can be a technically feasible option. Recently a trawler using only R-744 as a working fluid has been built and put into operation (Hafner, 2016). Systems using only R-744 as a refrigerant could potentially have a challenge to maintain the high energy efficiency when sea water temperatures are high. It is however expected that ejector-assisted systems can be utilised to overcome this challenge, in the same way as the ongoing development within commercial refrigeration systems using R-744 as refrigerant. Some such systems are already installed and under testing.

One of the advantages of the lower evaporation temperature (-48°C) obtained with R-744 as a refrigerant is a quicker freezing time and less damage to the fish at the surface due to softening of the surface during defrosting of the plate freezers. These benefits in fish quality are very much appreciated and therefore many ships are now converted to this solution especially in Europe, but now also in the US.

Hydrocarbons are also technically feasible refrigerants for on-board refrigeration, but the strict safety concerns and large refrigerant charge required make the practical application of flammable refrigerants aboard vessels unlikely.

The use of R-717 or R-744 in one of the three plant options analysed here is viable also in terms of overall climate change impact: when considering both the direct and indirect GHG emissions involved with the use of such plant alternatives (through TEWI, Total Equivalent Warming Impact) the assessment gives an impact reduction with respect to the existing situation (FRDC, 2013).

In any case, R-717 cannot be considered a viable solution for the replacement or retrofit of refrigeration plants on existing vessels without rebuilding. On the contrary, its choice is probably the right one when new ships are involved. R-744, on the contrary, can be a viable solutions both for new ships and for plant refurbishment in existing vessels, as some recent experiences have demonstrated (Hafner, 2016)

Just for sake of reference, the cost of an on-board R-717/R-744 cascade plant is estimated at 500k AUS$ for a new ship whose cost is 2.5M AUS$ or more (FRDC, 2013). In the markets where these plants are sold, the cost is on the same level as for HFC plants.

|  | Financial considerations |  | Technology risk (Complexity and performance) | Regulatory and environmental risk (10 years horizon) |
| --- | --- | --- | --- | --- |
|  | Capital investment | Operating expenses |  |  |
| Option 1 – Non-halocarbon refrigerants |  |  |  |  |
| R-717 system | Medium | Medium | High | Nil |
|  | Requires new ship with separate machine room or rebuilding | Potential improvement in efficiency. Require competence, but inexpensive refrigerant | Highly complex relative to on-board capabilities. Additional safety risk of ammonia (lower flammable and toxic). Training required in new markets | No environmental policy risk throughout expected life of equipment. |
| R-717/R-744 cascade system | Medium | Medium | High | Nil |
|  | Requires new ship with separate machine room or rebuilding | Potential improvement in efficiency. High maintenance cost due to complexity. Require competence, but inexpensive refrigerant | Highly complex relative to on-board capabilities. Additional safety risk of ammonia (lower flammable and toxic), Training required in new markets | No environmental policy risk throughout expected life of equipment. |
| R-744 system | Medium | Medium | Medium | Nil |
|  | Suitable for existing vessels with replacement of system | Potential improvement in efficiency at the expenses of complexity. Require competence, but inexpensive refrigerant | Some complexity relative to on-board capabilities. Training required in new markets | No environmental policy risk throughout expected life of equipment. |

### A2.4.3	Option 2 – Refrigerant replacement with plant adjustments

For systems with more than 10 to 15 years’ service life, it will generally not be feasible to perform just a refrigerant drop-in retrofit. Experience shows that compressors and other parts tend to break down shortly after a refrigerant retrofit. Replacement installations are therefore safer and more reliable. Reliability is usually one of the biggest concerns to ship owners as loss of cooling can be costly.

The most fundamental conversion is when the total system is converted to a NH3/CO2 solution. This type of conversion requires a major overhaul, because the safety conditions change when ammonia is involved. Also material compatibility is different when transiting from halocarbon refrigerants to ammonia.

A conversion from HCFC-22 to R-744 is a possible option as well, even if it requires a plant replacement.

Experience from the markets where these conversions to R-717 and R-744 have been done is that they can be done to the same cost as for a conversion to HFC.

A conversion to a haocarbon refrigerant could be feasible. As a matter of fact, the conversion from HCFC-22 to R-507A is investigated in (FRDC, 2013). This conversion would require the change of some components and other adjustments in the refrigeration systems in order to improve the efficiency and, necessarily, would require measures for leak containment. A conversion of this type is estimated to cost in the range of 250k to 280k AUS$ for the Northern Prawn Fishery fleet. But, R-507A (together with its companion R-404A) is not a low-GWP HFC (actually, its GWP is 4300 (UNEP, 2014)) and it cannot be considered a viable substitute anymore.

According to (UNEP, 2016) R-404A and R-507A are now being substituted for commercial refrigeration applications by blends such as R-448A and R-449A, which contain some HFOs and whose GWP is <1500. As is well known, the situation is evolving rapidly so it is not possible, at this stage, to name a refrigerant that will certainly be the definitive low-GWP substitute for R-507A or R-404A.

It may be reasonable, nevertheless, to expect in the medium term a solution that will make feasible the above-suggested type of conversion. The economics of the operation will, of course, depend on the cost of the new refrigerant. Most likely, the possible alternatives will be flammable in category A2 or A2L, thus requiring adequate safety considerations and precautions.

|  | Financial considerations |  | Technology risk (Complexity and performance) | Regulatory and environmental risk (10 years horizon) |
| --- | --- | --- | --- | --- |
|  | Capital investment | Operating expenses |  |  |
|  | Medium | Unknown | Unknown | Unknown |
| Option 2 – Refrigerant replacement with plant adjustments |  |  |  |  |
| Conventional refrigeration plant system operating with low-GWP HFC blend | Suitable for existing vessels with change of components and adjustments | Cost of refrigerants at present unknown flammability must be addressed | No significant change in type of technology and components | Environmental policy risk throughout expected life of equipment unknown at present |

### A2.4.4	Option 3 – Refrigerant drop-in

For systems with less than 10 to 15 years’ service life, then a refrigerant drop-in retrofit becomes a feasible option, provided there is such a drop-in. At present, actually, there is no low-GWP HFC available on the market that can be used as drop-in for on-board systems.

Some low-GWP HFC alternatives to HCFC-22 are proposed by the chemical industry as a drop-in for land-based applications (UNEP, 2015, UNEP 2016). When these alternatives become commercially available, they could be used also as HCFC-22 substitutes for on board applications. Considering the rapidly evolving situation in the development of low-GWP HFCs it may be probable that in a few years-time a satisfactory solution will also be available for this specific problem.

One aspect to be considered in cases concerning a step-by-step transition from HCFC-22 to HCF (both high-GWP and low-GWP) is how to meet regulatory requirement of product importers, especially when non-flagged vessels are involved.

|  | Financial considerations |  | Technology risk (Complexity and performance) | Regulatory and environmental risk (10 years horizon) |
| --- | --- | --- | --- | --- |
|  | Capital investment | Operating expenses |  |  |
|  | Unknown | Unknown | Unknown | Unknown |
| Option 3 – Refrigerant drop-in |  |  |  |  |
| Conventional refrigeration plant system operating with low-GWP HFC blend | Requires improvement of refrigerant containment | Cost of refrigerants at present unknown flammability must be addressed | No significant change in type of technology and components | Environmental policy risk throughout expected life of equipment unknown at present |

### A2.4.5	Option 4 – Maintaining HCFC-22

Considering the current problems in finding proper solutions for the retrofit of on-board systems equipped with HCFC-22, one reasonable option could be keeping it in the system for a further few years, until the end of the system or ship life.

The time horizon for this type of option should be no more than 4-5 years and the target should be those on-board plants with more than 10-15 years’ service life.

Maintaining HCFC-22 would require the contextual execution of the following operations: i) comprehensive upgrade for improved refrigerant containment, ii) increased focus on preventive maintenance regime, iii) securing sufficient stock of gas to be held in reserve, iv) planning for an inevitable capital equipment replacement program at the end of the period to a newly released low-GWP fluid to be assessed closer to the equipment replacement date. The literature source estimates the costs for this option at 30k-50k AUS$ plus the cost of gas reserves (FRDC, 2013).

Also for this option, one aspect to be considered is how to meet regulatory requirement of product importers, especially when non-flagged vessels are involved.

|  | Financial considerations |  | Technology risk (Complexity and performance) | Regulatory and environmental risk (10 years horizon) |
| --- | --- | --- | --- | --- |
|  | Capital investment | Operating expenses |  |  |
|  | Low | High | Low | Very high |
| Option 4 – Maintaining HCFC-22 |  |  |  |  |
| Existing plant, operating with HCFC-22, with improved containment Short term solution (max 4-5 years) May not be practical for all vessels | Requires improvement of refrigerant containment | HCFC-22 price expected to increase | No change in technology Availability of HCFC-22 will decrease | HFC-22 phase-out in advanced stages |

### A2.4.6	Ultra-low temperature solutions

Blast freezers for low temperature operations (-60°C and below) needed for sushi or sashimi grade tuna must use a cascade or two-stage compressor.

Table A2-3 (UNEP, 2014, UNEP, 2016) shows the situation of available refrigerants for cascade systems to be used on board ships.

Table A2-3 Refrigerants used on board ship in cascade systems

| Refrigerant | Normal Boiling Point (°C) | Cascade stage | GWP 100 years |
| --- | --- | --- | --- |
| HCFC-22 | -41 | 1 | 1780 |
| R-404A | -46.6/-45.8 | 1 | 4200 |
| R-407F | -46.1/-39.7 | 1 | 1800 |
| R-507A | -47.1 | 1 | 4300 |
| R-717 | -33.3 | 1 | 0 |
| HFC-23 | -82 | 2 | 12500 |
| R-508A | -87.4 | 2 | 12000 |
| R-508B | -87.4 | 2 | 12000 |
| R-744 | -56.2* | 2 | 1 |
| HC-170 | -89 | 2 | 5.5 |

*CO2 triple point is -56.2°C @ 5.2 bar

There are no viable low-GWP HFC alternatives to R-23, R-508A and R-508B, which are the refrigerants currently used in the low-temperature stage in cascade systems.

The new (unsaturated HFC) HFO compounds do not offer any low temperature solutions.

A possible alternative could technically be HC-170 (ethane, flammable, class A3), but its A3 flammability makes it unfeasible for on board systems.

A viable low-GWP alternative with evaporation down to -55°C, but requiring an equipment exchange, is an R-717/R-744 cascade system.

Another option could be a cascade system using NH3 in the high stage and HFC-32 in the low stage (the normal Boiling Point for HFC-32 is -52.0°C). The disadvantage is that the system will go to negative pressure at -70°C. This is a potential risk because air that enters can cause the refrigerant to explode.

It is possible to use a two-stage compressor to achieve low temperature blast freezing. The lowest evaporating temperature is -65°C @ +35°C condensing temperature. Evaporation will then happen at a sub-atmospheric pressure. Below is shown the possible operating envelop for such a system operating with R-407F. Also R-410A could be used in a two-stage compressor system.

In the medium term, a very interesting solution for the Ultra-Low temperature freezing can be the air-cycle (also known as Joule-Brayton reverse cycle). This is a non-vapour compression technology and fits better in the Not-In-Kind section, where it will be described and evaluated.

Figure A2-5 Limits for two stage compressor operating on R-407F

### A2.4.7	Land based equipment

Land based equipment for the fishing industry faces the same transition problems faced by other industrial refrigeration applications. Information on how to handle transition can be retrieved in the most recent reports produced by RTOC and TEAP Task Forces (UNEP, 2014, UNEP 2015, UNEP, 2016).

One peculiar characteristic of fishing industry land based installations is that all of them are inevitably connected to a water stream (sea, lake, river), which can be used as a machine coolant. This fact makes fishing industry less sensitive to high ambient temperatures (HAT) even when located in Parties with high ambient temperature conditions.

### A2.4.8	Not-In-Kind technologies

Provided that with the definition of “Not-In-Kind technologies” one refers to those refrigeration techniques which do not use vapour compression reverse cycle, there are some interesting options under study that deserve to be analysed to check if there is any possibility for their application within the fishing industry in the short term.

For very low temperatures, air (R-729) can be used as a working fluid in the so called air cycle, or Joule-Brayton reverse cycle. It was first proposed for ice making in 1844 by Dr. John Gorrie. The cycle was used for some years and then abandoned for absorption systems and later for compression systems.

The main reason for not using air was that the efficiency at the working conditions of most of refrigeration applications is far lower than the vapour compression efficiency. With modern motors and technologies, however, the air cycle can be a good solution when temperatures below -55°C are to be reached, especially if the refrigerant has to be non-flammable. Some interesting attempts of air cycle applications at low temperatures are available in the literature (Gigiel, 2006, Machida, 2011, Giannetti, 2015). To be available at a commercial level the technology needs more development work and therefore it can be a feasible option only in the medium to long term.

Absorption systems could also be a viable alternative to vapour compression, down to temperatures of -55°C. Systems could use the water (R-718)/ammonia (R-717) pair where water acts as solvent and ammonia as refrigerant. The same safety problems encountered with the application of vapour compression ammonia systems are to be faced here. Technology is mature and consolidated: the main problem with the absorption systems is the size and space needed on-board and the sensitivity to roll and pitch of a ship.

An important challenge for on board applications comes from the fact that driving energy is waste heat from engine and therefore there is a possible lack of cooling capacity if the ship’s engine is not working e.g. in harbour (Fernandez, 1998)

A lot of research in magnetic cooling is ongoing. The capacities with improving technology are increasing. It is a bit early in the development cycle to determine whether or not the cooling capacity will be sufficient and at the temperature differences needed on board modern fishing ships.

## A2.5		References

Awira, 2014	R. Awira, A. Dubrie, L. Rodwell, Refrigerant Consumption in Fishing Vessels operating in the Waters of Pacific islands Countries, OzonAction Special Issue 2014, available at: http://www.unep.org/ozonaction/Portals/105/documents/events/MOP26/OASI%202014%20low%20resolution.pdf

Awira, 2015	R. Awira, Refrigerant Consumption in Fishing Vessels operating in the Waters of Pacific Islands Countries, MOP27 Side Event, November 1, 2015, Conrad Hotel, Dubai, UAE, available at: http://www.unep.org/ozonaction/Portals/105/documents/events/MOP27/MOP27_RibanataakeAwira_PacificIslandsFisheriesForum-01Nov2015.pdf

de Larminat, 2015	P. de Larminat, The cold chain in the fishery sector. Refrigeration Technology Review, MOP27 Side Event, November 1, 2015, Conrad Hotel, Dubai, UAE, available at: http://www.unep.org/ozonaction/Portals/105/documents/events/MOP27/MOP-27_PauldeLarminat_Fisheries-01Nov2015.pdf

EUROSTAT, 2014	Agriculture, forestry and fishery statistics; Eurostat, 2014 edition

Faber, 2009	J. Faber et al.: Technical support for European action to reducing Greenhouse Gas Emissions from International maritime transport, Tender DG ENV.C3/ATA/2008/0016, available at: http://ec.europa.eu/clima/policies/transport/shipping/docs/ghg_ships_report_en.pdf

FAO, 2014	FAO, World Review of Fisheries and Aquaculture, Part 1, 2014, available at: http://www.fao.org/3/a-i3720e/i3720e01.pdf

Fernandez, 1998	J. Fernandez-Seara, A. Vales, M. Vasquez, Heat Recovery System to Power an Onboard NH3-H2O Absorption Plant in Trawler Chiller Fishing Vessel, Applied Thermal Engineering, Vol.18, pp.1189-1205, 1998

FRDC, 2013	Fisheries Research and Development Corporation, A study of refrigeration technology options for the Northern Prawn Fishery fleet and the Sydney Fish Market, FRDC 2013/227, November 2013, available at: http://frdc.com.au/research/Final_Reports/2013-227-DLD%20Appendix%20report.pdf

Giannetti, 2015	N.Giannetti, A.Milazzo, A.Rocchetti, Cascvade Refrigeration System with Inverse Brayton Cycle on the Cold Side, Proc. of 24th International Congress of Refrigeration, Yokohama, Japan, 2015

Gigiel, 2006	A.Gigiel, G. Giuliani, C. Vitale, F. Polonara, An open air cycle freezer,  Proc. of 7th Gustav Lorentzen Conf. on. Nat. Work. Fluids, pp. 325-328, Trondheim, Norway, 2006

Gillet, 2011	Gillett, R., Fisheries of the Pacific Islands. RAP Publication 2011/03. Bangkok, 2011. ISBN: 978-92-5-106792-5

Graham, 1992	J. Graham, W. A. Johnston and F. J. Nicholson, Ice Fisheries, FAO, 1992, ISBN 92-5-103280-7, available at: http://www.fao.org/docrep/T0713E/T0713E00.htm

Hafner, 2016	A. Hafner, Natural refrigerants, a complete solution – Latest technological advancements for warm climates, ATMOsphere Europe, Barcelona, Spain, 19-20 April 2016

Honolulu, 2015	Draft Report of the Western and Central Pacific Ocean Purse Seine Bigeye Management Workshop, Honolulu, Hawaii, Western Pacific Regional Fishery Management Council. April 8-10, 2015

Kawamura, 2015	K, Kawamura, Experiences in renewal of cold storage facilities from R22 to NH3/CO2 in Japan, Proc. of 24th International Congress of Refrigeration, Yokohama, Japan, 2015

Machida, 2011	A.Machida and J.Boone, Development of Air Refrigeration System “Pascal Air”, Proc. of 23rd International Congress of refrigeration, Prague, Czech Republic, 2011, ID:933

Nielsen, 2003	P.S.Nielsen et al., Introducing a new Ammonia/CO2 Cascade Concept for Large Fishing Vessels, 2003 International Institute of Ammonia Refrigeration Conference, Albuquerque, N.M.

Pachai, 2013	A.C.Pachai, From cradle to table ‐ Cooling and freezing of food, ICCC 2013, PARIS ‐ April 2‐4, 2013

The Pacific Community	The Pacific Community (SPC); FDS Manual chapter 4; available at: https://www.spc.int/coastfish/Sections/Development/FDSPublications/FDSManuals/HLL/HLL4s.pdf

UN, 2010	Resumed Review Conference on the Agreement Relating to the Conservation and Management of Straddling Fish Stocks and Highly Migratory Fish Stocks, New York, 24 – 28 May 2010

UNEP, 2014	UNEP, Refrigeration, AC and Heat Pumps Technical Options Committee, 2010 Assessment Report, ISBN 978-9966-076-09-0

UNEP, 2015	UNEP, Decision XXVI/9 Task Force Report – Additional Information on Alternatives to ozone Depleting Substances, March 2016, ISBN 978-9966-076-14-4

UNEP, 2016	UNEP, Decision XXVII/4 Task Force Report – Further Information on Alternatives to ozone Depleting Substances, March 2016, ISBN 978-9966-078-17-5

# Annex 3 - EU (F-gas, MAC Directive), USA (EPA SNAP Program) and Japan Regulatory Prohibitions (Ch. 6)

|  | European Union |  |  | United States |  |  | Japan |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Typical Historical Zero-ODP Option | Applications and Products | GWP Max Limit, F-gas Prohibited | Effective Date of Prohibition | Applications and Products | Unacceptable examples (GWP) | Date of Prohibition | Designated Products | Target GWP | Target Year |
| Mobile Air Conditioning |  |  |  |  |  |  |  |  |  |
| HFC-134a | Mobile Air Conditioners | 150 | 2013 (new types); 2017 (all) | Light-Duty Motor Vehicle Air Conditioners |  | MY 2021 (~1/6/2020) | Mobile Air Conditioners |  | 2023 |
| Stationary Air Conditioning and Refrigeration |  |  |  |  |  |  |  |  |  |
| HFC-134a, HC-600a | Domestic refrigerators & freezers | 150 | 2015 | Household refrigerators and freezers (Proposed) |  | 2021 |  |  |  |
| HFC-134a, R-404A | Commercial refrigerators and freezers (hermetically sealed systems) | 2500 | 2020 | Stand-alone Low-Temperature | R-404A (3922) | 2020 |  |  |  |
| HFC-134a, R-404A |  |  |  | Refrigerated Food Processing and Dispensing (Proposed) |  | 2021 |  |  |  |
| HFC-134a |  | 150 | 2022 | Stand-alone Medium-Temperature | HFC-134a (1430) | 2019 (<0.64 kW); 2020 (rest) |  |  |  |
| HFC-134a |  |  |  | Vending Machines | HFC-134a (1430) | 2019 |  |  |  |
| R-404A, R-407A, R-507 | Retail Food/ Supermarkets (Multipack centralized commercial refrigeration systems with a capacity 40kW or more) | 150 | 2022 | Retail food refrigeration (supermarket systems) | R-404A (3922), R-507A (3985) | 2017 | Condensing Unit and Refrigerating Unit (for separate type showcases, etc.) | 1500 | 2025 |
| R-404A | Retail Food/ Supermarkets (primary circuit of cascade systems) | 1500 | 2022 |  |  |  |  |  |  |
| R-717 | Cold Storage |  |  | Cold Storage Warehouses (Proposed) | R-404A (3922), R-407A (2107), R-410A (2088), R-507 (3985) | 2023 | Cold Storage Warehouses (>50,000 m3) | 100 | 2019 |
| HFC-134a | Chillers |  |  | Centrifugal Chillers (Proposed) | HFC-134a (1430) | 2024 | Commercial Air Conditioning (for offices and stores) [chillers, rooftop units, larger split systems] | 750 | 2020 |
| HFC-134a, R-407C R-410A |  |  |  | Positive Displacement Chillers (Proposed) | HFC-134a (1430), R-407C (1744), R-410A (2088) | 2024 |  |  |  |
| R-410A | Rooftop Units, Larger Split Systems |  |  |  |  |  |  |  |  |
| R-410A | Movable room air conditioning appliances (e.g. portable air conditioners, window units) | 150 | 2020 |  |  |  | Room Air Conditioning | 750 | 2018 |
| R-410A | Single split air conditioning systems containing < 3 kg of F-gases | 750 | 2025 |  |  |  |  |  |  |
| Fire Protection |  |  |  |  |  |  |  |  |  |
| HFC-227ea, CO2, Water, Dry Powder | Fire protection systems & fire extinguishers | HFC-23 | 2016 |  |  |  |  |  |  |
|  |  |  |  | Total flooding systems using C3F8 or C4F10 (Proposed) | PFC-218 (8830); PFC-3-1-10 (8860) | 2018 |  |  |  |
| HCs, HFC-134a | Tire Inflators | SF6, all HFCs | 4/7/2007 | Tire Inflators | HFC-134a (1430) | 20/7/2016 |  |  |  |
| HFC-134a, HFC-152a | Consumer product aerosols for entertainment and decorative purposes | 150 | 4/7/2009 | Consumer aerosols, with some exceptions for technical and medical aerosols | HFC-134a (1430) | 2016 | Dust Blowers | 10 | 2019 |
| HFC-134a, HFC-227ea (MDIs) | Technical aerosols (unless required to meet national safety standards or medical applications) | 150 | 2018 |  |  |  |  |  |  |
| Foams |  |  |  |  |  |  |  |  |  |
| HFC-134a, HFC-245fa, HFC-365mfc | XPS Foams with HFCs | 150 | 2023 | Polystyrene Extruded Boardstock and Billet (XPS) | HFC-134a (1430) | 2021 |  |  |  |
| HCs, HFC-134a | One-component foams | 150 | 4/7/2008 | Polyisocyanurate Laminated Boardstock, Polystyrene Extruded Sheet, Phenolic Insulation Board and Bunstock, Polyolefin, and several types of Polyurethane foams | HFC-134a (1430), HFC-245fa (1030), HFC-365mfc (794) | 2017-2020 | Urethane Foam (house construction materials) | 100 | 2020 |
| HCs, HFC-134a, HFC-245fa, HFC-365mfc | Other Foams with HFCs | 150 | 2020 |  |  |  |  |  |  |
| HFC-134a, HFC-245fa, HFC-365mfc | Other Foams (Rigid PU Spray Foam) | 150 | 2020 | Rigid PU Spray Foam (Proposed) | HFC-134a (1430), HFC-245fa (1030), HFC-365mfc (794) | 2020-2021 |  |  |  |

An

Notes:

- GWPs are AR4 values (IPCC, 2007)

- Prohibition dates January 1st unless otherwise noted and shown as day/month/year.

- Proposed USA prohibitions in italics; dates assume as proposed with a final rule published 1/1/2017.

- Exceptions include, inter alia, US mobile AC for export to markets lacking service infrastructure, EU stationary refrigeration products below -50 C, USA chillers for military vessels and human-rated spacecraft, EU foams where required to meet national safety standards, USA foams until 1/1/2022 (existing) or 1/1/2025 (proposed) for space- and aeronautics–related applications, and Japan exceptions to designated products.

# Annex 4 - Updated Tables for total, new manufacturing, and servicing demand

Below updated tables until 2050 (compared to 2030 in the XXVI/9 TF report) are given for the total demand, new manufacturing and servicing demand (data used for the scenario graphs in chapter 6):

- for non-Article 5 and Article 5 Parties

- for the major R/AC sub-sectors

- for the BAU, MIT-3 and MIT-5 scenarios:

- Table A4-1:  Demand in tonnes for new manufacturing plus servicing (total demand) for non-Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

- Table A4-2:  Demand in tonnes for new manufacturing only for non-Article 5 Parties for the period 2010-2050 for the six major sub-sectors and for the BAU, MIT-3 and MIT-5 scenarios

- Table A4-3:  Demand in tonnes for servicing only for non-Article 5 Parties for the period 2010-2050 for the six major sub-sectors and for the BAU, MIT-3 and MIT-5 scenarios

- Table A4-4:  Demand in ktonnes CO2-eq. for new manufacturing plus servicing (total demand) for non-Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

- Table A4-5:  Demand in ktonnes CO2-eq.for new manufacturing only for non-Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

- Table A4-6:  Demand in ktonnes CO2-eq.for servicing only for non-Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

- Table A4-7:  Demand in tonnes for servicing and new manufacturing (total demand) for Article 5 Parties for the period 2010-2050 for the six major sub-sectors and for the BAU, MIT-3 and MIT-5 scenarios

- Table A4-8:  Demand in tonnes for new manufacturing only for Article 5 Parties for the period 2010-2050 for the six major sub-sectors and for the BAU, MIT-3 and MIT-5 scenarios

- Table: A4-9:  Demand in tonnes for servicing only for Article 5 Parties for the period 2010-2050 for the six major sub-sectors and for the BAU, MIT-3 and MIT-5 scenarios

- Table A4-10:  Demand in ktonnes CO2-eq. for new manufacturing plus servicing (total demand) for Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

- Table A4-11:  Demand in ktonnes CO2-eq. for new manufacturing only for Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

- Table A4-12:  Demand in ktonnes CO2-eq. for servicing only for Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

Table A4-1:  Demand in tonnes for new manufacturing plus servicing (total demand) for non-Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

Table A4-2:  Demand in tonnes for new manufacturing only for non-Article 5 Parties for the period 2010-2050 for the six major sub-sectors and for the BAU, MIT-3 and MIT-5 scenarios

Table A4-3:  Demand in tonnes for servicing only for non-Article 5 Parties for the period 2010-2050 for the six major sub-sectors and for the BAU, MIT-3 and MIT-5 scenarios

Table A4-4:  Demand in ktonnes CO2-eq.for new manufacturing plus servicing (total demand) for non-Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

Table A4-5:  Demand in ktonnes CO2-eq. for new manufacturing only for non-Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

Table A4-6:  Demand in ktonnes CO2-eq. for servicing only for non-Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

Table A4-7:  Demand in tonnes for servicing and new manufacturing (total demand) for Article 5 Parties for the period 2010-2050 for the six major sub-sectors and for the BAU, MIT-3 and MIT-5 scenarios

Table A4-8:  Demand in tonnes for new manufacturing only for Article 5 Parties for the period 2010-2050 for the six major sub-sectors and for the BAU, MIT-3 and MIT-5 scenarios

Table: A4-9  Demand in tonnes for servicing only for Article 5 Parties for the period 2010-2050 for the six major sub-sectors and for the BAU, MIT-3 and MIT-5 scenarios

Table A4-10:  Demand in ktonnes CO2-eq. for new manufacturing plus servicing (total demand) for Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

Table A4-11:  Demand in ktonnes CO2-eq. for new manufacturing only for Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

Table A4-12:  Demand in ktonnes CO2-eq. for servicing only for Article 5 Parties for the period 2010-2050 and for the six major sub-sectors for the BAU, MIT-3 and MIT-5 scenarios

These are the four main HFCs currently used in the R/AC (including MACs) sector; HFC-134a is also used as a foam blowing agent, in MDIs and technical aerosols.

This section includes substantial contributions from J. Steven Brown, Ph.D., P.E., of The Catholic University of America, Washington, D.C., USA

The US and some Parties discussed a preliminary proposal at OEWG-37 that uses as criterion an average of at least two months per year over 10 consecutive years of a peak monthly average temperature above 35°C. Countrywide values in the dataset are calculated by taking a spatially weighted average of all weather stations within a country. The data were extracted from countrywide values in a dataset that are available from the Center of Environmental Data Analysis (CEDA). “Peak monthly average temperature” is calculated by finding the high temperature for each day in the month and averaging those daily highs to get an average peak temperature value for the month. The data source cited above refers to this as monthly average daily maximum temperature, and there are other ways to describe this criterion.